## Резерв
Количество по полю TAG | Расчет резерва |  |  |  |  | Количество по полю TAG | Расчет резерва | [5 empty] | BARRIER_MODEL | CABINET_MAR | Количество по полю CPU_NAME | STB_PART | CABINET_MAR | STB_NAME | MODULE_TYPE | CABINET_SYS | MODULE
IO type (Типовая схема подключения) | Пустой | Резерв | Сигнал | (пусто) | Питание | IO type (Типовая схема подключения) | Пустой | Резерв | Сигнал | (пусто) | Питание |  |  | 17-MC-DCS-001 | 199 |  | 17-MC-DCS-001 | O1010304R | AI713-H11 | 17-SC-DCS-001 | O1010000
DCS_AI_01 | #NULL! | 22.22% | 100% | #NULL! | #NULL! | DCS_AI_01 |  | 50 | 225 |  |  |  |  | 17-MC-DCS-002 | 160 |  | 17-MC-DCS-002 | O1010204 |  |  | O1010001
DCS_AI_02 | #NULL! | 27.59% | 100% | #NULL! | #NULL! | DCS_AI_02 |  | 16 | 58 |  |  |  |  | 17-MC-DCS-003 | 224 |  | 17-MC-DCS-006 | O1011000 |  |  | O1010002
DCS_AI_03 | #NULL! | 25% | 100% | #NULL! | #NULL! | DCS_AI_03 |  | 3 | 12 |  |  |  |  | 17-MC-DCS-004 | 313 |  | 17-MC-DCS-007 | O1011114 |  |  | O1010003
DCS_AI_04 | #NULL! | 40% | 100% | #NULL! | #NULL! | DCS_AI_04 |  | 2 | 5 |  |  |  |  | 17-MC-DCS-005 | 224 |  | 17-MC-DCS-008 | (пусто) |  |  | O1010004
DCS_AI_05 | #NULL! | 20% | 100% | #NULL! | #NULL! | DCS_AI_05 |  | 1 | 5 |  |  |  |  | 17-MC-DCS-006 | 8 | TUA711-AIO16 | 17-MC-DCS-006 | O1010000 |  |  | O1010005
DCS_AO_01 | #NULL! | 25% | 100% | #NULL! | #NULL! | DCS_AO_01 |  | 1 | 4 |  |  |  |  | 17-MC-DCS-007 | 194 |  |  | O1010001 |  |  | O1010006
DCS_AO_02 | #NULL! | 25.61% | 100% | #NULL! | #NULL! | DCS_AO_02 |  | 21 | 82 |  |  |  |  | 17-MC-DCS-008 | 7 |  |  | O1010002 |  |  | O1010007
DCS_DI_01 | #NULL! | 25.11% | 100% | #NULL! | #NULL! | DCS_DI_01 |  | 56 | 223 |  |  |  |  | 17-MC-DCS-009 | 29 |  |  | O1010003 |  |  | O1010008
DCS_DI_02 | #NULL! | 20.21% | 100% | #NULL! | #NULL! | DCS_DI_02 |  | 39 | 193 |  |  |  | GS8555-EX | 17-MC-DCS-007 | 3 |  |  | O1010004 |  |  | O1010009
DCS_DI_03 | #NULL! | 20.18% | 100% | #NULL! | #NULL! | DCS_DI_03 |  | 68 | 337 |  |  |  | HD5516 | 17-MC-DCS-001 | 27 |  |  | O1010005 |  |  | O1010010
DCS_DI_04 | #NULL! | 22.22% | 100% | #NULL! | #NULL! | DCS_DI_04 |  | 4 | 18 |  |  |  |  | 17-MC-DCS-002 | 143 |  |  | O1010006 |  |  | O1010011
DCS_DO_01 | #NULL! | 23.76% | 100% | #NULL! | #NULL! | DCS_DO_01 |  | 43 | 181 |  |  |  |  | 17-MC-DCS-004 | 39 |  |  | O1010007 |  |  | O1010012R
DCS_DO_02 | #NULL! | 190.9% | 100% | #NULL! | #NULL! | DCS_DO_02 |  | 21 | 11 |  |  |  |  | 17-MC-DCS-009 | 23 |  |  | O1010008 |  |  | O1010014R
DCS_DO_03 | #NULL! | 30.8% | 100% | #NULL! | #NULL! | DCS_DO_03 |  | 69 | 224 |  |  |  | HD5542 | 17-MC-DCS-006 | 178 |  |  | O1010012R |  |  | O1010100R
DCS_PI_01 | #NULL! | 50% | 100% | #NULL! | #NULL! | DCS_PI_01 |  | 1 | 2 |  |  |  |  | 17-MC-DCS-007 | 11 |  |  | O1010014R |  |  | O1010102R
(пусто) |  | #NULL! |  | #NULL! |  | (пусто) | 23 |  |  |  | 1 |  |  | 17-MC-DCS-008 | 116 |  |  | O1010104R |  | 17-SC-DCS-002 | O1011000
|  | #NULL! |  | #NULL! | #NULL! |  | 90 | [6 empty] | 17-MC-DCS-009 | 66 |  |  | O1010106R |  |  | O1011001
DCS_DI_05 | #NULL! | 106.1% | 100% | #NULL! | #NULL! | DCS_DI_05 |  | 35 | 33 |  |  |  | HD5546 | 17-MC-DCS-006 | 49 |  |  | O1010114 |  |  | O1011002
DCS_DO_04 | #NULL! | 22.73% | 100% | #NULL! | #NULL! | DCS_DO_04 |  | 5 | 22 |  |  |  |  | 17-MC-DCS-008 | 38 |  |  | O1011000 |  |  | O1011003
DCS_DI_07 | #NULL! | 28.57% | 100% | #NULL! | #NULL! | DCS_DI_07 |  | 2 | 7 |  |  |  |  | 17-MC-DCS-009 | 21 |  |  | O1011012R |  |  | O1011004
[13 empty] | HD5573 | 17-MC-DCS-006 | 6 |  | 17-MC-DCS-007 | O1011008R |  |  | O1011005
Количество по полю TAG | Расчет резерва |  |  |  |  | Количество по полю TAG |  | Расчет резерва |  |  |  |  | KFD2-ER-1.W.LB | 17-MC-DCS-001 | 5 |  | 17-MC-DCS-008 | O1010009 |  |  | O1011006
CLASS_TYPE_SIG | Пустой | Резерв | Сигнал | (пусто) | Питание | CLASS_TYPE_SIG | STB_PART | Пустой | Резерв | Сигнал | (пусто) | Питание |  | 17-MC-DCS-002 | 17 |  |  | O1010010 |  |  | O1011008R
AI-IS (4-20 mA, 2 wire) DCS | #NULL! | 26.32% | 100% | #NULL! | #NULL! | AI-IS (4-20 mA, 2 wire) DCS | TUA711-AIO16 |  | 10 | 38 |  |  | (пусто) | 17-MC-DCS-001 | 25 |  |  | O1010100R |  |  | O1011010R
AI-NIS (4-20 mA, 2 wire) DCS | #NULL! | 21.39% | 100% | #NULL! | #NULL! | AI-NIS (4-20 mA, 2 wire) DCS | TUA711-AIO16 |  | 40 | 187 |  |  |  | 17-MC-DCS-005 | 32 |  |  | O1010108R |  |  | O1011300R
AI-NIS (4-20 mA, 4 wire) DCS | #NULL! | 25% | 100% | #NULL! | #NULL! | AI-NIS (4-20 mA, 4 wire) DCS | TUA711-AIO16 |  | 3 | 12 |  |  |  | 17-MC-DCS-006 | 15 |  |  | O1011001 | AO713-H11 | 17-SC-DCS-001 | O1010104R
AI-R-IS (4-20 mA, 2 wire) DCS | #NULL! | 33.33% | 100% | #NULL! | #NULL! | AI-R-IS (4-20 mA, 2 wire) DCS | TUA711-AIO16 |  | 4 | 12 |  |  |  | 17-MC-DCS-008 | 15 |  |  | O1011002 |  |  | O1010106R
AI-R-IS (4-20 mA, 4 wire) DCS | #NULL! | 100% | 100% | #NULL! | #NULL! | AI-R-IS (4-20 mA, 4 wire) DCS | TUA711-AIO16 |  | 1 | 1 |  |  |  | 17-MC-DCS-009 | 5 |  |  | O1011003 |  |  | O1010108R
AI-R-NIS |  | #NULL! |  | #NULL! | #NULL! | AI-R-NIS | TUA711-AIO16 | 14 | [5 empty] | (пусто) |  |  |  | O1011004 |  |  | O1010110R
AI-R-NIS (4-20 mA, 2 wire) DCS | #NULL! | 26.09% | 100% | #NULL! | #NULL! | AI-R-NIS (4-20 mA, 2 wire) DCS | TUA711-AIO16 |  | 12 | 46 | [7 empty] | O1011010R |  |  | O1010112R
AI-R-NIS (4-20 mA, 4 wire) DCS | #NULL! | 25% | 100% | #NULL! | #NULL! | AI-R-NIS (4-20 mA, 4 wire) DCS | TUA711-AIO16 |  | 1 | 4 | [7 empty] | O1011014R |  |  | O1010114
AI-RTD-NIS (3 wire) DCS | #NULL! | 20% | 100% | #NULL! | #NULL! | AI-RTD-NIS (3 wire) DCS | TUA711-AIO16 |  | 1 | 5 | [7 empty] | O1011302R |  | 17-SC-DCS-002 | O1011012R
AO-NIS |  | #NULL! |  | #NULL! | #NULL! | AO-NIS | TUA711-AIO16 | 11 | [8 empty] | 17-MC-DCS-009 | O1010011 |  |  | O1011014R
AO-NIS (4-20 mA) DCS | #NULL! | 25% | 100% | #NULL! | #NULL! | AO-NIS (4-20 mA) DCS | TUA711-AIO16 |  | 1 | 4 | [7 empty] | O1010102R |  |  | O1011302R
AO-R-IS |  | #NULL! |  | #NULL! | #NULL! | AO-R-IS | TUA711-AIO16 | 11 | [9 empty] | O1010110R | DI715-S11 | 17-SC-DCS-001 | O1010115
AO-R-IS (4-20 mA) DCS | #NULL! | 50% | 100% | #NULL! | #NULL! | AO-R-IS (4-20 mA) DCS | TUA711-AIO16 |  | 7 | 14 | [7 empty] | O1010112R |  |  | O1010200
AO-R-NIS |  | #NULL! |  | #NULL! | #NULL! | AO-R-NIS | TUA711-AIO16 | 14 | [9 empty] | O1011005 |  |  | O1010201
AO-R-NIS (4-20 mA) DCS | #NULL! | 20.59% | 100% | #NULL! | #NULL! | AO-R-NIS (4-20 mA) DCS | TUA711-AIO16 |  | 14 | 68 | [7 empty] | O1011006 |  |  | O1010202
DI-IS |  | #NULL! |  | #NULL! | #NULL! | DI-IS | TUA711-DIO32 | 9 | [9 empty] | O1011300R |  |  | O1010203
DI-IS (NAMUR) DCS | #NULL! | 21.05% | 100% | #NULL! | #NULL! | DI-IS (NAMUR) DCS | TUA711-DIO32 |  | 4 | 19 | [5 empty] | TUA711-DIO32 | 17-MC-DCS-001 | O1010203 |  |  | O1010204
DI-NIS (Conductivity) DCS | #NULL! | 22.22% | 100% | #NULL! | #NULL! | DI-NIS (Conductivity) DCS | TUA711-DIO32 |  | 4 | 18 | [6 empty] | 17-MC-DCS-002 | O1011100 |  |  | O1010205
DI-NIS (Diagnostic) DCS | #NULL! | 13.11% | 100% | #NULL! | #NULL! | DI-NIS (Diagnostic) DCS | TUA711-DIR32 |  | 8 | 61 | [7 empty] | O1011101 |  |  | O1010206
DI-NIS (NAMUR) DCS | #NULL! | 20.39% | 100% | #NULL! | #NULL! | DI-NIS (NAMUR) DCS | TUA711-DIO32 |  | 31 | 152 | [7 empty] | O1011102 |  |  | O1010207
DI-NIS (Thermistors PTC) DCS | #NULL! | 18.18% | 100% | #NULL! | #NULL! | DI-NIS (Thermistors PTC) DCS | TUA711-DIO32 |  | 4 | 22 | [7 empty] | O1011103 |  |  | O1010208
DI-NIS (VFC) DCS | #NULL! | 29.63% | 100% | #NULL! | #NULL! | DI-NIS (VFC) DCS | TUA711-DIR32 |  | 48 | 162 | [7 empty] | O1011104 |  |  | O1010209
DO-NIS (24VDC) DCS | #NULL! | 23.76% | 100% | #NULL! | #NULL! | DO-NIS (24VDC) DCS | TUA711-DOR32 |  | 43 | 181 | [6 empty] | 17-MC-DCS-003 | O1010206 |  |  | O1010300
DO-NIS (VFC NO) DCS | #NULL! | 190.9% | 100% | #NULL! | #NULL! | DO-NIS (VFC NO) DCS | TUA711-DOR32 |  | 21 | 11 | [7 empty] | O1010207 |  |  | O1010301
PI-R-NIS (Pulse Input) DCS | #NULL! | 50% | 100% | #NULL! | #NULL! | PI-R-NIS (Pulse Input) DCS | TUA711-AIO16 |  | 1 | 2 | [7 empty] | O1010208 |  |  | O1010304R
(пусто) |  | #NULL! |  | #NULL! | #NULL! | (пусто) |  | 23 | [9 empty] | O1010212 |  | 17-SC-DCS-002 | O1011100
Питание | #NULL! | #NULL! |  | #NULL! |  |  | (пусто) | [10 empty] | O1010213 |  |  | O1011101
AI-R-IS |  | #NULL! |  | #NULL! | #NULL! | Питание | [5 empty] | 1 | [5 empty] | O1010214 |  |  | O1011102
AI-NIS |  | #NULL! |  | #NULL! | #NULL! | AI-R-IS | TUA711-AIO16 | 14 | [9 empty] | O1011213 |  |  | O1011103
DI-NIS (MCC) DCS 230 VAC | #NULL! | 20.18% | 100% | #NULL! | #NULL! | AI-NIS |  | 8 | [8 empty] | 17-MC-DCS-004 | O1010205 |  |  | O1011104
DI-NIS (MCC) DCS 220 VDC | #NULL! | 106.1% | 100% | #NULL! | #NULL! | DI-NIS (MCC) DCS 230 VAC | TUA711-DIO32 |  | 68 | 337 | [7 empty] | O1010301 |  |  | O1011105
DO-NIS (MCC) DCS 230 VAC | #NULL! | 30.8% | 100% | #NULL! | #NULL! | DI-NIS (MCC) DCS 220 VDC | TUA711-DIO32 |  | 35 | 33 | [7 empty] | O1011106 |  |  | O1011106
DO-NIS (MCC) DCS 220 VDC | #NULL! | 22.73% | 100% | #NULL! | #NULL! | DO-NIS (MCC) DCS 230 VAC | TUA711-DIO32 |  | 69 | 224 | [7 empty] | O1011107 |  |  | O1011107
DI-NIS (24VDC) DCS | #NULL! | 28.57% | 100% | #NULL! | #NULL! | DO-NIS (MCC) DCS 220 VDC | TUA711-DIO32 |  | 5 | 22 | [7 empty] | O1011108 |  |  | O1011108
DI-NIS |  | #NULL! |  | #NULL! | #NULL! | DI-NIS (24VDC) DCS | TUA711-DIR32 |  | 2 | 7 | [7 empty] | O1011109 |  |  | O1011109
[6 empty] | DI-NIS |  | 9 | [9 empty] | O1011110 |  |  | O1011110
[18 empty] | O1011205 |  |  | O1011111
[18 empty] | O1011206 |  |  | O1011112
[18 empty] | O1011207 |  |  | O1011113
[18 empty] | O1011208 |  |  | O1011114
[17 empty] | 17-MC-DCS-005 | O1010115 |  |  | O1011115
[18 empty] | O1010209 |  |  | O1011200
[18 empty] | O1010215 |  |  | O1011201
[18 empty] | O1010300 |  |  | O1011304
[18 empty] | O1011111 | DO716-S11 | 17-SC-DCS-001 | O1010210
[18 empty] | O1011112 |  |  | O1010211
[18 empty] | O1011209 |  |  | O1010212
[18 empty] | O1011304 |  |  | O1010213
[17 empty] | 17-MC-DCS-009 | O1011115 |  |  | O1010214
[16 empty] | TUA711-DIR32 | 17-MC-DCS-001 | O1010200 |  |  | O1010215
[18 empty] | O1010201 |  | 17-SC-DCS-002 | O1011202
[18 empty] | O1010202 |  |  | O1011203
[18 empty] | O1010304R |  |  | O1011204
[17 empty] | 17-MC-DCS-002 | O1010204 |  |  | O1011205
[18 empty] | O1011105 |  |  | O1011206
[17 empty] | 17-MC-DCS-007 | O1011113 |  |  | O1011207
[18 empty] | O1011114 |  |  | O1011208
[18 empty] | O1011200 |  |  | O1011209
[18 empty] | O1011201 |  |  | O1011210
[16 empty] | TUA711-DOR32 | 17-MC-DCS-001 | O1010210 |  |  | O1011211
[18 empty] | O1010211 |  |  | O1011212
[18 empty] | O1011212 |  |  | O1011213
[17 empty] | 17-MC-DCS-002 | O1011202 | (пусто) | (пусто) | (пусто)
O1011203
O1011204
[17 empty] | 17-MC-DCS-007 | O1011210
O1011211
[16 empty] | (пусто) | (пусто) | (пусто)

## Tag Assignment
| Позиция прибора | Имя тэга |  | Класс и тип сигнала | [7 empty] | Полевой кабель |  |  | Кроссовый шкаф | [10 empty] | Системный шкаф | [13 empty] | Система | [21 empty] | Маркировка проводов
Рев. |  |  | Логическая диаграмма |  |  |  | Тип прибора | Схема P__ID | (Типовая схема подключения |  | Питание | Наименование кабеля | Тип кабеля | № жил | Шкаф | Полевой клеммник | Номер клемм под полевой кабель |  |  |  | Тип клемм | Имя барьера | Модель барьера | Системная плата | Тип терминальной платы | Имя Системного кабеля | Заказной системного кабеля | Шкаф | Контроллер |  | Адрес базовой платы | Слот | № слота | Канал | Модуль | [5 empty] | Наименование_ENG | Наименование_RU | [31 empty] | Для сигналов
rev | LOOP | TAG | ID | CLASS_TYPE_SIG | Внесенные изменения | Расчет резерва | Instrument_Type_Desc | P__ID_Drawing | IO type (Типовая схема подключения) | Instrument_Location | Loop_External_power | CAB_NAME | CAB_TYPE | Set_Name | CABINET_MAR | FTS_NAME | FTS_TERM1 | FTS_TERM2 | FTS_TERM3 | MAX TERMINAL | FTS_TYPE | BARRIER_NAME | BARRIER_MODEL | STB_NAME | STB_PART | SYS_CABLE | SYSTEM_CABLE_PART | CABINET_SYS | CPU_NAME | Номер коммуникационного модуля | RACK | MODULE | SLOT | CHANNEL | MODULE_TYPE | Канальность | Потребление | Комментарий ГКС | Изменения на объекте | SYSTEM | TAG_SERVICE | TAG_SERVICE_RU | ASSET | SubAsset | Plant_Name | LINK | State_ON | State_OFF | Plant_Name | ALARM_SET_POINT_LL | ALARM_SET_POINT_L | ALARM_SET_POINT_H | ALARM_SET_POINT_HH | DCS_Range_Minimum | DCS_Range_Maximum | DCS_Range_Units | 3 | 1 | 2 | 2 | 3 | от полевой клеммы до барьера белый | от полевой клеммы до барьера черный | от полевой клеммы до барьера черный 2 | 2 | от терм. платы до барьера белый | от терм. платы до барьера черный | 2 | от полевой клеммы до терм. платы белый | от полевой клеммы до терм. платы черный | 1 | 1 | 2 | Доп. поле [9] ru_RU | Доп. поле [10] ru_RU | Доп. поле [13] ru_RU | Доп. поле [14] ru_RU | Доп. поле [15] ru_RU | Доп. поле [17] ru_RU | Доп. поле [18] ru_RU | Доп. поле [19] ru_RU | Доп. поле [20] ru_RU | сцеп1 | сцеп2 | сцеп3 | сцеп4
01 | 10-F -08003 | 10FSH08003 |  | DI-NIS (VFC) DCS |  | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08003 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-05 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-001 AMMONIA RECOVERY | SS-001 РЕКУПЕРАЦИЯ АММИАКА | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-05:1/ O1011105:11A | TS-Q-05:2/ O1011105:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-F -08004 | 10FSH08004 |  | DI-NIS (VFC) DCS |  | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 11-C-DD-N-001FL10 | 06 Pair | Pr.01 | 17-MC-DCS-002 | TS-O-10 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-002 COMPRESSOR BUILDING | SS-002 ЗДАНИЕ КОМПРЕССОРА | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-10:1/ O1011105:1A | TS-O-10:2/ O1011105:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-F -08005 | 10FSH08005 |  | DI-NIS (VFC) DCS |  | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 11-C-DD-N-001FL10 | 06 Pair | Pr.02 | 17-MC-DCS-002 | TS-O-10 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-003 COMPRESSOR BUILDING | SS-003 ЗДАНИЕ КОМПРЕССОРА | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-10:3/ O1011105:2A | TS-O-10:4/ O1011105:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.6 | 10-F -08006 | 10FSH08006 |  | DI-NIS (VFC) DCS | 06.03.25 изм кабель с 11-C-DD-N-001FL20 (Pr.01) - добавлен новый индивидуальный кабель по TQ-112 | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08006 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-P-11 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 3 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-Q-14 клеммы 1, 2 смонтироват ьновую клеммную группу, провода от клеммной группы до терм панели | DCS AMMONIA-UTILITIES | SS-004 DEAERATOR, BFW PUMPS UNIT | SS-004 ДЕАЭРАТОР, НАСОСНЫЙ БЛОК BFW | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-11:1/ O1011105:3A | TS-P-11:2/ O1011105:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-F -08007 | 10FSH08007 |  | DI-NIS (VFC) DCS |  | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08007 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-06 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-005 METHANATION, PC UNIT | SS-005 МЕТАНИРОВАНИЕ, БЛОК ПК | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-06:1/ O1011105:12A | TS-Q-06:2/ O1011105:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-F -08008 | 10FSH08008 |  | DI-NIS (VFC) DCS |  | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08008 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-07 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-006 REFORMER AND STM GEN AREA | SS-006 РЕФОРМАТОР И ЗОНА ГЕНЕРАТОРА STM | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-07:1/ O1011105:13A | TS-Q-07:2/ O1011105:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.3 | 10-F -08010 | 10FSH08010 |  | DI-NIS (VFC) DCS | изм номер клеммной группы (TQ_074) | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 11-C-DD-N-001FL40 | 06 Pair | Pr.01 | 17-MC-DCS-002 | TS-P-07 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-007 SHIFT CONVERTER AREA | SS-007 ОБЛАСТЬ ПРЕОБРАЗОВАТЕЛЯ ПЕРЕДАЧ | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-07:1/ O1011105:6A | TS-P-07:2/ O1011105:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.6 | 10-F -08011 | 10FSH08011 |  | DI-NIS (VFC) DCS | 06.03.25 изм кабель с 11-C-DD-N-001FL20 (Pr.02) - добавлен новый индивидуальный кабель TQ-112 | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08011 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-P-12 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 4 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-Q-14 клеммы 3,4 смонтироват ьновую клеммную группу, провода от клеммной группы до терм панели | DCS AMMONIA-UTILITIES | SS-008 CO2 RECOVERY AREA | SS-008 ЗОНА УЛУЧШЕНИЯ CO2 | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-12:1/ O1011105:4A | TS-P-12:2/ O1011105:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.3 | 10-F -08012 | 10FSH08012 |  | DI-NIS (VFC) DCS | изм номер клеммной группы (TQ_074) | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 11-C-DD-N-002FL50 | 06 Pair | Pr.01 | 17-MC-DCS-002 | TS-P-08 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-009 CO2 RECOVERY AREA | SS-009 ЗОНА РЕКУПЕРАЦИИ CO2 | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-08:1/ O1011105:7A | TS-P-08:2/ O1011105:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-F -08013 | 10FSH08013 |  | DI-NIS (VFC) DCS |  | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08013 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-08 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-010 AMMONIA SYNTHESIS UNIT | SS-010 УСТАНОВКА СИНТЕЗА АММИАКА | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-08:1/ O1011105:14A | TS-Q-08:2/ O1011105:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.6 | 10-F -08014 | 10FSH08014 |  | DI-NIS (VFC) DCS | 06.03.25 изм кабель с11-C-DD-N-001FL30 (Pr.01) - добавлен новый индивидуальный кабель TQ-112 | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08014 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-P-13 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 5 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-O-09 клеммы 1,2 смонтироват ьновую клеммную группу, провода от клеммной группы до терм панели | DCS AMMONIA-UTILITIES | SS-011 AMMONIA SYNTHESIS UNIT | SS-011 УСТАНОВКА СИНТЕЗА АММИАКА | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-13:1/ O1011105:5A | TS-P-13:2/ O1011105:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.8 |  | Резерв |  | DI-NIS (VFC) DCS | сигнал 10FSH08015, кабель 10-FSH-08015 перенесен в WTU по TQ_Ammonia-122 | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 15 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-Q-09, клеммы 1, 2 до терм платы | DCS AMMONIA-UTILITIES |  |  | 10-GENERAL - COMM | 00-Common | [38 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-F -08016 | 10FSH08016 |  | DI-NIS (VFC) DCS |  | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08016 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-10 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-013 CW PUMP STATION & FILTERS | SS-013 НАСОСНАЯ СТАНЦИЯ CW И ФИЛЬТРЫ | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-10:1/ O1011105:16A | TS-Q-10:2/ O1011105:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-F -08017 | 10FSH08017 |  | DI-NIS (VFC) DCS |  | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08017 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-11 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-014 CHEMICAL STORAGE | SS-014 ХРАНЕНИЕ ХИМИКАТОВ | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-11:1/ O1011105:17A | TS-Q-11:2/ O1011105:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-F -08019 | 10FSH08019 |  | DI-NIS (VFC) DCS |  | Сигнал | Flow Switch | 4124-XZ-DM-21008004 | DCS_DI_01 | Field |  | 10-FSH-08019 | 01 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-12 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SS-015 DEMI WATER UNIT | SS-015 БЛОК ДЕМИ-ВОДЫ | 10-GENERAL - COMM | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-12:1/ O1011105:18A | TS-Q-12:2/ O1011105:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08011 | 10MXSA08011 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21008001 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.17 | 17-MC-DCS-001 | TS-F-05 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08011 ДОСТУПЕН | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:33/ O1010201:17A | TS-F-05:34/ O1010201:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08011 | 10MXSR08011 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21008001 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.18 | 17-MC-DCS-001 | TS-F-05 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08011 ПО МЕСТУ/ДИСТАНЦИЯ | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:35/ O1010201:18A | TS-F-05:36/ O1010201:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08011 | 10MZSH08011 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21008001 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.19 | 17-MC-DCS-001 | TS-F-05 | 37 | 38 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08011 ОТКРЫТО (СИГН) | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:37/ O1010201:19A | TS-F-05:38/ O1010201:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08011 | 10MZSL08011 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21008001 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.20 | 17-MC-DCS-001 | TS-F-05 | 39 | 40 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08011 ЗАКРЫТО (СИГН) | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:39/ O1010201:20A | TS-F-05:40/ O1010201:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08011 | 10MXYSP08011 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21008001 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.13 | 17-MC-DCS-001 | TS-G-05 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 13 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08011 ОСТАНОВИТЬ | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-05:13/ O1010211:13A | TS-G-05:14/ O1010211:13C | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08011 | 10MXYH08011 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21008001 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.15 | 17-MC-DCS-001 | TS-G-05 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 14 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08011 ОТКРЫТЬ | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-05:15/ O1010211:14A | TS-G-05:16/ O1010211:14C | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08011 | 10MXYL08011 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21008001 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.17 | 17-MC-DCS-001 | TS-G-05 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 15 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08011 ЗАКРЫТЬ | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-05:17/ O1010211:15A | TS-G-05:18/ O1010211:15C | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08012 | 10MXSA08012 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21008001 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.15 | 17-MC-DCS-002 | TS-R-03 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08012 ДОСТУПЕН | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:29/ O1010204:9A | TS-R-03:30/ O1010204:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08012 | 10MXSR08012 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21008001 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.16 | 17-MC-DCS-002 | TS-R-03 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08012 ПО МЕСТУ/ДИСТАНЦИЯ | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:31/ O1010204:10A | TS-R-03:32/ O1010204:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08012 | 10MZSH08012 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21008001 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.17 | 17-MC-DCS-002 | TS-R-03 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08012 ОТКРЫТО (СИГН) | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:33/ O1010204:11A | TS-R-03:34/ O1010204:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08012 | 10MZSL08012 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21008001 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.18 | 17-MC-DCS-002 | TS-R-03 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08012 ЗАКРЫТО (СИГН) | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:35/ O1010204:12A | TS-R-03:36/ O1010204:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08012 | 10MXYSP08012 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21008001 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.19 | 17-MC-DCS-001 | TS-G-05 | 19 | 20 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 16 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08012 ОСТАНОВИТЬ | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-05:19/ O1010211:16A | TS-G-05:20/ O1010211:16C | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08012 | 10MXYH08012 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21008001 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.21 | 17-MC-DCS-001 | TS-G-05 | 21 | 22 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 17 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08012 ОТКРЫТЬ | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-05:21/ O1010211:17A | TS-G-05:22/ O1010211:17C | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 10-M -08012 | 10MXYL08012 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21008001 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.23 | 17-MC-DCS-001 | TS-G-05 | 23 | 24 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 18 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Fire Water to Cooling Water Towers | 10-MOV-08012 ЗАКРЫТЬ | 10-AMMONIA PRODUCTION PLANT - GENERAL - COMMON | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-05:23/ O1010211:18A | TS-G-05:24/ O1010211:18C | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020200 | 17AT020200 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.01 | 17-MC-DCS-008 | TS-O-01 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011002_U1 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet process condensate | НЕКОНДЕНЦИОННЫЙ КОНДЕНСАТ НА КАТИОНИТЫ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 45 |  | 0 | 50 | μS/cm | [5 empty] | TS-O-01:1/ O1011002_U1:3 | TS-O-01:2/ O1011002_U1:4 |  |  | O1011002:1A/ O1011002_U1:5 | O1011002:1C/ O1011002_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020200 | 17AY020200 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL03-L022 | 30 Core | C.11 | 17-MC-DCS-002 | TS-O-01 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 6 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-01:11/ O1011202:6A | TS-O-01:12/ O1011202:6C | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020201 | 17AT020201 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | PH Analyzer | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.02 | 17-MC-DCS-008 | TS-O-01 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011002_U2 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet process condensate | НЕКОНДЕНЦИОННЫЙ КОНДЕНСАТ НА КАТИОНИТЫ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 8 |  | 0 | 14 | pH | [5 empty] | TS-O-01:3/ O1011002_U2:3 | TS-O-01:4/ O1011002_U2:4 |  |  | O1011002:2A/ O1011002_U2:5 | O1011002:2C/ O1011002_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020201 | 17AY020201 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL03-L022 | 30 Core | C.13 | 17-MC-DCS-002 | TS-O-01 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 7 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-01:13/ O1011202:7A | TS-O-01:14/ O1011202:7C | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020202 -A | 17AT020202A |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.05 | 17-MC-DCS-008 | TS-O-01 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011002_U3 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet SAC Cationic Exchanger | ВЫХОД КАТИОНИТА S-021А | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 50 |  |  | 0 | 200 | μS/cm | [5 empty] | TS-O-01:9/ O1011002_U3:3 | TS-O-01:10/ O1011002_U3:4 |  |  | O1011002:3A/ O1011002_U3:5 | O1011002:3C/ O1011002_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020202 -A | 17AY020202A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL03-L022 | 30 Core | C.15 | 17-MC-DCS-002 | TS-O-01 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 8 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-01:15/ O1011202:8A | TS-O-01:16/ O1011202:8C | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020202 -B | 17AT020202B |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.10 | 17-MC-DCS-008 | TS-O-01 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U1 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet SAC Cationic Exchanger | ВЫХОД КАТИОНИТА S-021В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 50 |  |  | 0 | 200 | μS/cm | [5 empty] | TS-O-01:19/ O1011003_U1:3 | TS-O-01:20/ O1011003_U1:4 |  |  | O1011003:1A/ O1011003_U1:5 | O1011003:1C/ O1011003_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020202 -B | 17AY020202B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL03-L022 | 16 Core | C.11 | 17-MC-DCS-002 | TS-O-03 | 11 | 12 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 22 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-03:11/ O1011202:22A | TS-O-03:12/ O1011202:22C | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020202 -C | 17AT020202C |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.15 | 17-MC-DCS-008 | TS-O-01 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U4 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet SAC Cationic Exchanger | ВЫХОД КАТИОНИТА S-021С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 50 |  |  | 0 | 200 | μS/cm | [5 empty] | TS-O-01:29/ O1011003_U4:3 | TS-O-01:30/ O1011003_U4:4 |  |  | O1011003:4A/ O1011003_U4:5 | O1011003:4C/ O1011003_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020202 -C | 17AY020202C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL03-L022 | 16 Core | C.11 | 17-MC-DCS-002 | TS-O-04 | 11 | 12 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 28 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-04:11/ O1011202:28A | TS-O-04:12/ O1011202:28C | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020203 | 17AT020203 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | PH Analyzer | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.01 | 17-MC-DCS-008 | TS-O-03 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011004_U1 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet Mixed beds | ВХОД В ФСД S-022А/В/С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 8 |  | 0 | 14 | pH | [5 empty] | TS-O-03:1/ O1011004_U1:3 | TS-O-03:2/ O1011004_U1:4 |  |  | O1011004:1A/ O1011004_U1:5 | O1011004:1C/ O1011004_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020203 | 17AY020203 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.19 | 17-MC-DCS-002 | TS-O-06 | 19 | 20 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 16 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:19/ O1011203:16A | TS-O-06:20/ O1011203:16C | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020204 -A | 17AT020204A |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.04 | 17-MC-DCS-008 | TS-O-03 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011002_U6 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet Mixed Bed | ВЫХОД С ФСД S-022А | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.2 |  | 0 | 1 | μS/cm | [5 empty] | TS-O-03:7/ O1011002_U6:3 | TS-O-03:8/ O1011002_U6:4 |  |  | O1011002:6A/ O1011002_U6:5 | O1011002:6C/ O1011002_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020204 -A | 17AY020204A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.19 | 17-MC-DCS-002 | TS-O-05 | 19 | 20 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 6 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:19/ O1011203:6A | TS-O-05:20/ O1011203:6C | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020204 -B | 17AT020204B |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.09 | 17-MC-DCS-008 | TS-O-03 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U7 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet Mixed Bed | ВЫХОД С ФСД S-022В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.2 |  | 0 | 1 | μS/cm | [5 empty] | TS-O-03:17/ O1011003_U7:3 | TS-O-03:18/ O1011003_U7:4 |  |  | O1011003:7A/ O1011003_U7:5 | O1011003:7C/ O1011003_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020204 -B | 17AY020204B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.17 | 17-MC-DCS-002 | TS-O-06 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 15 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:17/ O1011203:15A | TS-O-06:18/ O1011203:15C | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020204 -C | 17AT020204C |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.14 | 17-MC-DCS-008 | TS-O-03 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U10 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet Mixed Bed | ВЫХОД С ФСД S-022С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.2 |  | 0 | 1 | μS/cm | [5 empty] | TS-O-03:27/ O1011003_U10:3 | TS-O-03:28/ O1011003_U10:4 |  |  | O1011003:10A/ O1011003_U10:5 | O1011003:10C/ O1011003_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020204 -C | 17AY020204C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.17 | 17-MC-DCS-002 | TS-P-01 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 26 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:17/ O1011203:26A | TS-P-01:18/ O1011203:26C | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020205 | 17AT020205A |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | SiO2 Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_03 | Field | 230 VAC | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.18 | 17-MC-DCS-008 | TS-O-03 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011002_U9 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet Mixed beds | ВЫХОД С ФСД S-022А | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 20 | ppb | [5 empty] | TS-O-03:35/ O1011002_U9:1 | TS-O-03:36/ O1011002_U9:2 |  |  | O1011002:9A/ O1011002_U9:5 | O1011002:9C/ O1011002_U9:6 | [6 empty] | 9A | 9C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020205 | 17AT020205B |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | SiO2 Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_03 | Field | 230 VAC | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.19 | 17-MC-DCS-008 | TS-O-03 | 37 | 38 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U13 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet Mixed beds | ВЫХОД С ФСД S-022В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 20 | ppb | [5 empty] | TS-O-03:37/ O1011003_U13:1 | TS-O-03:38/ O1011003_U13:2 |  |  | O1011003:13A/ O1011003_U13:5 | O1011003:13C/ O1011003_U13:6 | [6 empty] | 13A | 13C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020205 | 17AT020205C |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | SiO2 Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_03 | Field | 230 VAC | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.20 | 17-MC-DCS-008 | TS-O-03 | 39 | 40 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U14 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet Mixed beds | ВЫХОД С ФСД S-022С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 20 | ppb | [5 empty] | TS-O-03:39/ O1011003_U14:1 | TS-O-03:40/ O1011003_U14:2 |  |  | O1011003:14A/ O1011003_U14:5 | O1011003:14C/ O1011003_U14:6 | [6 empty] | 14A | 14C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020205 | 17AT020205D |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | SiO2 Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_03 | Field | 230 VAC | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.21 | 17-MC-DCS-008 | TS-O-03 | 41 | 42 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011004_U3 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet Mixed beds | ВЫХОД С ФСД S-022А/В/С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 20 | ppb | [5 empty] | TS-O-03:41/ O1011004_U3:1 | TS-O-03:42/ O1011004_U3:2 |  |  | O1011004:3A/ O1011004_U3:5 | O1011004:3C/ O1011004_U3:6 | [6 empty] | 3A | 3C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020205 | 17AY020205A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.19 | 17-MC-DCS-002 | TS-P-01 | 19 | 20 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 27 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:19/ O1011203:27A | TS-P-01:20/ O1011203:27C | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020205 | 17AY020205B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.21 | 17-MC-DCS-002 | TS-P-01 | 21 | 22 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 28 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:21/ O1011203:28A | TS-P-01:22/ O1011203:28C | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020205 | 17AY020205C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.23 | 17-MC-DCS-002 | TS-P-01 | 23 | 24 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 29 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:23/ O1011203:29A | TS-P-01:24/ O1011203:29C | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020205 | 17AY020205D |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.25 | 17-MC-DCS-002 | TS-P-01 | 25 | 26 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 30 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:25/ O1011203:30A | TS-P-01:26/ O1011203:30C | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020206 | 17AT020206 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.17 | 17-MC-DCS-008 | TS-O-03 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011004_U2 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet Mixed beds | ВЫХОД С ФСД S-022А/В/С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.2 | 0.25 | 0 | 1 | μS/cm | [5 empty] | TS-O-03:33/ O1011004_U2:3 | TS-O-03:34/ O1011004_U2:4 |  |  | O1011004:2A/ O1011004_U2:5 | O1011004:2C/ O1011004_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020206 | 17AY020206 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.21 | 17-MC-DCS-002 | TS-O-06 | 21 | 22 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 17 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:21/ O1011203:17A | TS-O-06:22/ O1011203:17C | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020207 | 17AT020207 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL03-L022 | 12 Pair | Pr.08 | 17-MC-DCS-008 | TS-O-06 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011004_U4 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 to SAC & MB | РАСТВОР H2SO4 НА РЕГЕНЕРАЦИЮ S-021/S-022 | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 165 | 260 |  | 0 | 500 | mS/cm | [5 empty] | TS-O-06:15/ O1011004_U4:3 | TS-O-06:16/ O1011004_U4:4 |  |  | O1011004:4A/ O1011004_U4:5 | O1011004:4C/ O1011004_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020207 | 17AY020207 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DO_01 | Field |  | 17-C-CD-N-007FL03-L022 | 30 Core | C.13 | 17-MC-DCS-002 | TS-P-03 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 17 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-03:13/ O1011204:17A | TS-P-03:14/ O1011204:17C | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020208 | 17AT020208 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL03-L022 | 12 Pair | Pr.09 | 17-MC-DCS-008 | TS-O-06 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011004_U5 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | NaOH to MB | NAOH РАСТВОР NAOH НА РЕГЕНЕРАЦИЮ S-022 | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 150 | 250 |  | 0 | 500 | mS/cm | [5 empty] | TS-O-06:17/ O1011004_U5:3 | TS-O-06:18/ O1011004_U5:4 |  |  | O1011004:5A/ O1011004_U5:5 | O1011004:5C/ O1011004_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020208 | 17AY020208 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DO_01 | Field |  | 17-C-CD-N-007FL03-L022 | 30 Core | C.15 | 17-MC-DCS-002 | TS-P-03 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 18 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-03:15/ O1011204:18A | TS-P-03:16/ O1011204:18C | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020209 | 17AT020209 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | PH Analyzer | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_AI_01 | Field |  | 17-C-AD-N-006FL03-L022 | 24 Pair | Pr.03 | 17-MC-DCS-008 | TS-P-03 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011004_U11 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet neutralizatiom pumps 024A/B | НЕЙТРАЛИЗАЦИОННЫЕ СТОКИ ОТ Р-024A/B | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 8 |  | 0 | 14 | pH | [5 empty] | TS-P-03:5/ O1011004_U11:3 | TS-P-03:6/ O1011004_U11:4 |  |  | O1011004:11A/ O1011004_U11:5 | O1011004:11C/ O1011004_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020209 | 17AY020209 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-010FL03-L022 | 30 Core | C.09 | 17-MC-DCS-002 | TS-P-04 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 23 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-04:9/ O1011204:23A | TS-P-04:10/ O1011204:23C | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020210 | 17AT020210 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | PH Analyzer | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_AI_01 | Field |  | 17-C-AD-N-006FL03-L022 | 24 Pair | Pr.04 | 17-MC-DCS-008 | TS-P-03 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011004_U12 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet neutralizatiom pumps 024A/B | НЕЙТРАЛИЗАЦИОННЫЕ СТОКИ ОТ Р-024A/B | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 8 |  | 0 | 14 | pH | [5 empty] | TS-P-03:7/ O1011004_U12:3 | TS-P-03:8/ O1011004_U12:4 |  |  | O1011004:12A/ O1011004_U12:5 | O1011004:12C/ O1011004_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020210 | 17AY020210 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-010FL03-L022 | 30 Core | C.11 | 17-MC-DCS-002 | TS-P-04 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 24 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-04:11/ O1011204:24A | TS-P-04:12/ O1011204:24C | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020211 | 17AT020211 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | PH Analyzer | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_AI_01 | Field |  | 17-C-AD-N-006FL03-L022 | 24 Pair | Pr.05 | 17-MC-DCS-008 | TS-P-03 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011004_U13 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet neutralizatiom pumps 025A/B | НЕЙТРАЛИЗАЦИОННЫЕ СТОКИ ОТ Р-025A/B | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 8 |  | 0 | 14 | pH | [5 empty] | TS-P-03:9/ O1011004_U13:3 | TS-P-03:10/ O1011004_U13:4 |  |  | O1011004:13A/ O1011004_U13:5 | O1011004:13C/ O1011004_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020211 | 17AY020211 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-010FL03-L022 | 30 Core | C.13 | 17-MC-DCS-002 | TS-P-04 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 25 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-04:13/ O1011204:25A | TS-P-04:14/ O1011204:25C | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -020212 | 17AT020212 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | PH Analyzer | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_AI_01 | Field |  | 17-C-AD-N-006FL03-L022 | 24 Pair | Pr.06 | 17-MC-DCS-008 | TS-P-03 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011004_U14 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Outlet neutralizatiom pumps 025A/B | НЕЙТРАЛИЗАЦИОННЫЕ СТОКИ ОТ Р-025A/B | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 8 |  | 0 | 14 | pH | [5 empty] | TS-P-03:11/ O1011004_U14:3 | TS-P-03:12/ O1011004_U14:4 |  |  | O1011004:14A/ O1011004_U14:5 | O1011004:14C/ O1011004_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -020212 | 17AY020212 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-010FL03-L022 | 30 Core | C.15 | 17-MC-DCS-002 | TS-P-04 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 26 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Analyzer sample line | ЛИНИЯ ОТБОРА ПРОБ АНАЛИЗАТОРА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-04:15/ O1011204:26A | TS-P-04:16/ O1011204:26C | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -03020 | 17AT03020CV |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.01 | 17-MC-DCS-006 | TS-Q-04 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010004_U13 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Urea Melt Steam Condensate | ПАРОВЫЙ КОНД ИЗ КАРБАМИДА В Т-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100 | µS/cm | [5 empty] | TS-Q-04:1/ O1010004_U13:3 | TS-Q-04:2/ O1010004_U13:4 |  |  | O1010004:13A/ O1010004_U13:5 | O1010004:13C/ O1010004_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -03020 | 17FSL03020CV |  | DI-NIS (VFC) DCS |  | Сигнал | Low Flow Switch (Flow) | 4124-XZ-DM-21703004 | DCS_DI_01 | Field |  | 17-C-DD-N-004FL10 | 12 Pair | Pr.02 | 17-MC-DCS-001 | TS-G-08 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Urea Melt Steam Condensate | Конденсат пара из расплава мочевины | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ACTIVE | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-08:3/ O1010201:29A | TS-G-08:4/ O1010201:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -03021 | 17AT03021CV |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.02 | 17-MC-DCS-006 | TS-Q-04 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010004_U14 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | ТУРБ КОНДЕНСАТ В T-030/T-031 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100 | µS/cm | [5 empty] | TS-Q-04:3/ O1010004_U14:3 | TS-Q-04:4/ O1010004_U14:4 |  |  | O1010004:14A/ O1010004_U14:5 | O1010004:14C/ O1010004_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -03021 | 17FSL03021CV |  | DI-NIS (VFC) DCS |  | Сигнал | Low Flow Switch (Flow) | 4124-XZ-DM-21703004 | DCS_DI_01 | Field |  | 17-C-DD-N-004FL10 | 12 Pair | Pr.03 | 17-MC-DCS-001 | TS-G-08 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | Конденсат пара турбины к 17-Т-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ACTIVE | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-08:5/ O1010201:30A | TS-G-08:6/ O1010201:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -03022 | 17AT03022CV |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.03 | 17-MC-DCS-006 | TS-Q-04 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010004_U15 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | ТУРБ КОНДЕНСАТ С КАРБАМИДА В T-030/T-031 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100 | µS/cm | [5 empty] | TS-Q-04:5/ O1010004_U15:3 | TS-Q-04:6/ O1010004_U15:4 |  |  | O1010004:15A/ O1010004_U15:5 | O1010004:15C/ O1010004_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -03022 | 17FSL03022CV |  | DI-NIS (VFC) DCS |  | Сигнал | Low Flow Switch (Flow) | 4124-XZ-DM-21703004 | DCS_DI_01 | Field |  | 17-C-DD-N-004FL10 | 12 Pair | Pr.04 | 17-MC-DCS-001 | TS-G-08 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | Конденсат пара турбины к 17-Т-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ACTIVE | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-08:7/ O1010201:31A | TS-G-08:8/ O1010201:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -03023 | 17AT03023CV |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.04 | 17-MC-DCS-006 | TS-Q-04 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010004_U16 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Process Condensate from 17-P-030 A/B/C | НЕКОНДИЦ КОНД ОТ P-030-A/B/C В Т-031 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100 | µS/cm | [5 empty] | TS-Q-04:7/ O1010004_U16:3 | TS-Q-04:8/ O1010004_U16:4 |  |  | O1010004:16A/ O1010004_U16:5 | O1010004:16C/ O1010004_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -03023 | 17FSL03023CV |  | DI-NIS (VFC) DCS |  | Сигнал | Low Flow Switch (Flow) | 4124-XZ-DM-21703004 | DCS_DI_01 | Field |  | 17-C-DD-N-004FL10 | 12 Pair | Pr.05 | 17-MC-DCS-001 | TS-G-08 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Process Condensate from 17-P-030 A/B/C | Технологический конденсат из 17-P-030 A/B/C | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ACTIVE | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-08:9/ O1010201:32A | TS-G-08:10/ O1010201:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -03064 | 17AT03064CV |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-XZ-DM-21703003 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.05 | 17-MC-DCS-006 | TS-Q-04 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U2 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-031A/B/C discharge to 17-S-022A/B/C | КОНДЕНСАТ ОТ Р-031А/В/С НА ФСД | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100 | µS/cm | [5 empty] | TS-Q-04:9/ O1010005_U2:3 | TS-Q-04:10/ O1010005_U2:4 |  |  | O1010005:2A/ O1010005_U2:5 | O1010005:2C/ O1010005_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -03064 | 17FSL03064CV |  | DI-NIS (VFC) DCS |  | Сигнал | Low Flow Switch (Flow) | 4124-XZ-DM-21703003 | DCS_DI_01 | Field |  | 17-C-DD-N-004FL10 | 12 Pair | Pr.01 | 17-MC-DCS-001 | TS-G-08 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-031A/B/C discharge to 17-S-022A/B/C | 17-P-031A/B/C разряжается в 17-S-022A/B/C | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ACTIVE | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-08:1/ O1010201:28A | TS-G-08:2/ O1010201:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -07002 | 17AY07002 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21707001 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.01 | 17-MC-DCS-006 | TS-Q-03 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010106R_U3 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 3 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CWR from distribution header | ООВ ОТ РАСПРЕД КОЛЛЕКТОРА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:1/ O1010106R_U3:3 | TS-Q-03:2/ O1010106R_U3:4 |  |  | O1010106R:3A/ O1010106R_U3:5 | O1010106R:3C/ O1010106R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -07003 | 17AT07003PH |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | PH Analyzer | 4124-FY-VD-BD17217L07300001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL07-L073 | 12 Pair | Pr.04 | 17-MC-DCS-006 | TS-Q-02 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010002_U5 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-023 CW Chemical Treatment | ПРОДУВКА ВОЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6.5 | 9 |  | 0 | 14 | % | [5 empty] | TS-Q-02:7/ O1010002_U5:3 | TS-Q-02:8/ O1010002_U5:4 |  |  | O1010002:5A/ O1010002_U5:5 | O1010002:5C/ O1010002_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -07003 | 17AT07003RO |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Analyzer Transmitter | 4124-FY-VD-BD17217L07300001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL07-L073 | 12 Pair | Pr.05 | 17-MC-DCS-006 | TS-Q-02 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010002_U6 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-023 CW Chemical Treatment | ПРОДУВКА ВОЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 300 | 600 |  | 0 | 1000 | % | [5 empty] | TS-Q-02:9/ O1010002_U6:3 | TS-Q-02:10/ O1010002_U6:4 |  |  | O1010002:6A/ O1010002_U6:5 | O1010002:6C/ O1010002_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -07003 | 17AT07003CV |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-FY-VD-BD17217L07300001 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL07-L073 | 12 Pair | Pr.06 | 17-MC-DCS-006 | TS-Q-02 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010012R_U10 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | To 17-L-073 Chemical Treatment Control Unit | ПРОДУВКА ВОЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  | 90 | 0 | 100 | % | [5 empty] | TS-Q-02:11/ O1010012R_U10:3 | TS-Q-02:12/ O1010012R_U10:4 |  |  | O1010012R:10A/ O1010012R_U10:5 | O1010012R:10C/ O1010012R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -090301 | 17AT090301A |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-GY-VD-BD17517L091091_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-I-004FL10-L091 | 12 Pair | Pr.04 | 17-MC-DCS-009 | TS-G-04 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U12 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From DECISSANT TOWER | ВЫХОД ОСУШИТЕЛЕЙ ВОЗДУХА КИП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -100 | 20 | °C | [5 empty] | TS-G-04:7/ O1010011_U12:3 | TS-G-04:8/ O1010011_U12:4 |  |  | O1010011:12A/ O1010011_U12:5 | O1010011:12C/ O1010011_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -090301 | 17AT090301B |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-GY-VD-BD17517L091091_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-I-004FL10-L091 | 12 Pair | Pr.05 | 17-MC-DCS-009 | TS-G-04 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U13 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From DECISSANT TOWER | ВЫХОД ОСУШИТЕЛЕЙ ВОЗДУХА КИП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -100 | 20 | °C | [5 empty] | TS-G-04:9/ O1010011_U13:3 | TS-G-04:10/ O1010011_U13:4 |  |  | O1010011:13A/ O1010011_U13:5 | O1010011:13C/ O1010011_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -11101 | 17AT11101CV |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.01 | 17-MC-DCS-009 | TS-H-03 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U8 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | BFW from 17-U-111 to 17-P-111A/B/C | ПИТАТЕЛЬНАЯ ВОДА КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 10 |  | 0 | 100 | µS/cm | [5 empty] | TS-H-03:1/ O1011006_U8:3 | TS-H-03:2/ O1011006_U8:4 |  |  | O1011006:8A/ O1011006_U8:5 | O1011006:8C/ O1011006_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -11101 | 17AT11101PH |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.02 | 17-MC-DCS-009 | TS-H-03 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U10 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | BFW from 17-U-111 to 17-P-111A/B/C | ПИТАТЕЛЬНАЯ ВОДА КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 9 | 10 |  | 2 | 12 | pH | [5 empty] | TS-H-03:3/ O1011006_U10:3 | TS-H-03:4/ O1011006_U10:4 |  |  | O1011006:10A/ O1011006_U10:5 | O1011006:10C/ O1011006_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -11101 | 17AT11101V |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.03 | 17-MC-DCS-009 | TS-H-03 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U11 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | BFW from 17-U-111 to 17-P-111A/B/C | ПИТАТЕЛЬНАЯ ВОДА КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 10 |  | 0 | 20 | ppb | [5 empty] | TS-H-03:5/ O1011006_U11:3 | TS-H-03:6/ O1011006_U11:4 |  |  | O1011006:11A/ O1011006_U11:5 | O1011006:11C/ O1011006_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -11101 | 17FSL11101 |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21711101 | DCS_DI_02 | Field |  | 17-FSL -11101 | 01 Pair | Pr.01 | 17-MC-DCS-009 | TS-G-08 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A | O1011115_U2 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | BFW from 17-U-111 to 17-P-111A/B/C | BFW от 17-U-111 до 17-P-111A/B/C | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ACTIVE | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-08:1/ O1011115_U2:3 | TS-G-08:2/ O1011115_U2:4 |  |  | O1011115:2A/ O1011115_U2:5 | O1011115:2B/ O1011115_U2:6 | [6 empty] | 2A | 2B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -11301 | 17AT11301X |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 03.04.25 изм тип сигнала, типовая схема с DCS_AI_01 | Сигнал | Analyzer Transmitter (Analyzer) | 4124-XZ-DM-21711301 | DCS_AI_03 | Field |  | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.01 | 17-MC-DCS-006 | TS-R-05 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U1 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 1 | AI713-H11 | 16 |  | Потребл мощн - 2,28 kW | переподключить провода от полевых клемм с контактов барьера 3+ и 4- на контакты барьера 1+ и 2- | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | ДЫМОВЫЕ ГАЗЫ ПУСКОВОГО КОТЛА L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 200 | ppm | [5 empty] | TS-R-05:1/ O1010007_U1:1 | TS-R-05:2/ O1010007_U1:2 |  |  | O1010007:1A/ O1010007_U1:5 | O1010007:1C/ O1010007_U1:6 | [6 empty] | 1A | 1C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -11301 | 17AT11301Y |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 03.04.25 изм тип сигнала, типовая схема с DCS_AI_01 | Сигнал | Analyzer Transmitter (Analyzer) | 4124-XZ-DM-21711301 | DCS_AI_03 | Field |  | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.02 | 17-MC-DCS-006 | TS-R-05 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U2 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 2 | AI713-H11 | 16 |  | Потребл мощн - 2,28 kW | переподключить провода от полевых клемм с контактов барьера 3+ и 4- на контакты барьера 1+ и 2- | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | ДЫМОВЫЕ ГАЗЫ ПУСКОВОГО КОТЛА L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 20 | mol% | [5 empty] | TS-R-05:3/ O1010007_U2:1 | TS-R-05:4/ O1010007_U2:2 |  |  | O1010007:2A/ O1010007_U2:5 | O1010007:2C/ O1010007_U2:6 | [6 empty] | 2A | 2C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -11301 | 17AT11301AC |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 03.04.25 изм тип сигнала, типовая схема с DCS_AI_01 | Сигнал | Analyzer Transmitter (Analyzer) | 4124-XZ-DM-21711301 | DCS_AI_03 | Field |  | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.03 | 17-MC-DCS-006 | TS-R-05 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U3 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 3 | AI713-H11 | 16 |  | Потребл мощн - 2,28 kW | переподключить провода от полевых клемм с контактов барьера 3+ и 4- на контакты барьера 1+ и 2- | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | ДЫМОВЫЕ ГАЗЫ ПУСКОВОГО КОТЛА L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100 | ppm | [5 empty] | TS-R-05:5/ O1010007_U3:1 | TS-R-05:6/ O1010007_U3:2 |  |  | O1010007:3A/ O1010007_U3:5 | O1010007:3C/ O1010007_U3:6 | [6 empty] | 3A | 3C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -11301 | 17AT11301AW |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 03.04.25 изм тип сигнала, типовая схема с DCS_AI_01 | Сигнал | Analyzer Transmitter (Analyzer) | 4124-XZ-DM-21711301 | DCS_AI_03 | Field |  | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.04 | 17-MC-DCS-006 | TS-R-05 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U4 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 4 | AI713-H11 | 16 |  | Потребл мощн - 2,28 kW | переподключить провода от полевых клемм с контактов барьера 3+ и 4- на контакты барьера 1+ и 2- | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | ДЫМОВЫЕ ГАЗЫ ПУСКОВОГО КОТЛА L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 50 | ppm | [5 empty] | TS-R-05:7/ O1010007_U4:1 | TS-R-05:8/ O1010007_U4:2 |  |  | O1010007:4A/ O1010007_U4:5 | O1010007:4C/ O1010007_U4:6 | [6 empty] | 4A | 4C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -11301 | 17AT11301V |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 03.04.25 изм тип сигнала, типовая схема с DCS_AI_01 | Сигнал | Analyzer Transmitter (Analyzer) | 4124-XZ-DM-21711301 | DCS_AI_03 | Field |  | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.05 | 17-MC-DCS-006 | TS-R-05 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U5 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 5 | AI713-H11 | 16 |  | Потребл мощн - 2,28 kW | переподключить провода от полевых клемм с контактов барьера 3+ и 4- на контакты барьера 1+ и 2- | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | ДЫМОВЫЕ ГАЗЫ ПУСКОВОГО КОТЛА L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 10 | mol% | [5 empty] | TS-R-05:9/ O1010007_U5:1 | TS-R-05:10/ O1010007_U5:2 |  |  | O1010007:5A/ O1010007_U5:5 | O1010007:5C/ O1010007_U5:6 | [6 empty] | 5A | 5C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -11301 | 17AT11301R |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 03.04.25 изм тип сигнала, типовая схема с DCS_AI_01 | Сигнал | Analyzer Transmitter (Analyzer) | 4124-XZ-DM-21711301 | DCS_AI_03 | Field |  | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.06 | 17-MC-DCS-006 | TS-R-05 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U6 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 6 | AI713-H11 | 16 |  | Потребл мощн - 2,28 kW | переподключить провода от полевых клемм с контактов барьера 3+ и 4- на контакты барьера 1+ и 2- | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | ДЫМОВЫЕ ГАЗЫ ПУСКОВОГО КОТЛА L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 50 | mol% | [5 empty] | TS-R-05:11/ O1010007_U6:1 | TS-R-05:12/ O1010007_U6:2 |  |  | O1010007:6A/ O1010007_U6:5 | O1010007:6C/ O1010007_U6:6 | [6 empty] | 6A | 6C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 | 17-A -11301 | 17HS11301MN |  | DI-NIS (VFC) DCS | 30.05.2024 изм вид сигнала с DO | Сигнал | Hand Switch - Maintenance (General) | 4124-XZ-DM-21711301 | DCS_DI_01 | RR-AM |  | 17-C-DD-N-001FL11-AH001 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-18 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 13 | DI715-S11 | 32 |  | 30.05.2024 изм вид сигнала с DO, изм клеммник |  | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | 17-AH-001 СИСТЕМА НЕПРЕРЫВНОГО МОНИТОРИНГА ВЫБРОСОВ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | CEMS | NO ACTION | 0 | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-18:3/ O1011114:13A | TS-F-18:4/ O1011114:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02 | 17-A -11301 | 17HS11301ON |  | DI-NIS (VFC) DCS | 30.05.2024 изм вид сигнала с DO | Сигнал | Hand Switch - On Line (General) | 4124-XZ-DM-21711301 | DCS_DI_01 | RR-AM |  | 17-C-DD-N-001FL11-AH001 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-18 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 14 | DI715-S11 | 32 |  | 30.05.2024 изм вид сигнала с DO, изм клеммник |  | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | 17-AH-001 СИСТЕМА НЕПРЕРЫВНОГО МОНИТОРИНГА ВЫБРОСОВ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | CEMS | NO ACTION | 0 | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-18:1/ O1011114:14A | TS-F-18:2/ O1011114:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -113647 | 17AT113647 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Analyzer Transmitter | 4124-FB-VD-BD00317L11111388 | DCS_AI_01 | Field |  | 17-C-AD-N-001-LP003-L111 | 12 Pair | Pr.01 | 17-MC-DCS-006 | TS-Q-08 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010004_U8 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Specific Conductivity | КОТЛОВАЯ ВОДА L-111-V-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 200 | uS/cm | [5 empty] | TS-Q-08:1/ O1010004_U8:3 | TS-Q-08:2/ O1010004_U8:4 |  |  | O1010004:8A/ O1010004_U8:5 | O1010004:8C/ O1010004_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -113648 | 17AT113648 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Analyzer Transmitter | 4124-FB-VD-BD00317L11111388 | DCS_AI_01 | Field |  | 17-C-AD-N-001-LP003-L111 | 12 Pair | Pr.02 | 17-MC-DCS-006 | TS-Q-08 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010004_U9 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | pH Analysis | КОТЛОВАЯ ВОДА L-111-V-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 8 | 12 | pH | [5 empty] | TS-Q-08:3/ O1010004_U9:3 | TS-Q-08:4/ O1010004_U9:4 |  |  | O1010004:9A/ O1010004_U9:5 | O1010004:9C/ O1010004_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -113649 | 17AT113649 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Analyzer Transmitter | 4124-FB-VD-BD00317L11111388 | DCS_AI_01 | Field |  | 17-C-AD-N-001-LP003-L111 | 12 Pair | Pr.03 | 17-MC-DCS-006 | TS-Q-08 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010004_U10 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Acid Conductivity sampling | НАСЫЩЕННЫЙ ПАР L-111-V-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1 | uS/cm | [5 empty] | TS-Q-08:5/ O1010004_U10:3 | TS-Q-08:6/ O1010004_U10:4 |  |  | O1010004:10A/ O1010004_U10:5 | O1010004:10C/ O1010004_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -113650 | 17AT113650A |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 30.05.2024 изм тег, тип сигнала на актив | Сигнал | Analyzer Transmitter | #N/A | DCS_AI_03 | Field | 230 VAC | 17-C-AD-N-001-LP003-L111 | 12 Pair | Pr.04 | 17-MC-DCS-006 | TS-Q-08 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010004_U11 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Silica sampling | НАСЫЩЕННЫЙ ПАР L-111-V-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 70 | ppb | [5 empty] | TS-Q-08:7/ O1010004_U11:1 | TS-Q-08:8/ O1010004_U11:2 |  |  | O1010004:11A/ O1010004_U11:5 | O1010004:11C/ O1010004_U11:6 | [6 empty] | 11A | 11C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -113651 | 17AT113651 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Analyzer Transmitter | 4124-FB-VD-BD00317L11111388 | DCS_AI_01 | Field |  | 17-C-AD-N-001-LP003-L111 | 12 Pair | Pr.06 | 17-MC-DCS-006 | TS-Q-08 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010004_U12 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Acid Conductivity sampling | ПЕРЕГРЕТЫЙ ПАР ПУСКОВОГО КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1 | uS/cm | [5 empty] | TS-Q-08:11/ O1010004_U12:3 | TS-Q-08:12/ O1010004_U12:4 |  |  | O1010004:12A/ O1010004_U12:5 | O1010004:12C/ O1010004_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A -17101 | 17AT17101CV |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-XZ-DM-21717101 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.01 | 17-MC-DCS-008 | TS-O-02 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011001_U1 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate to Distribution Header | ПАРОВЫЙ КОНДЕНСАТ ИЗ Е-171 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 15 |  | 0 | 100 | µS/cm | [5 empty] | TS-O-02:1/ O1011001_U1:3 | TS-O-02:2/ O1011001_U1:4 |  |  | O1011001:1A/ O1011001_U1:5 | O1011001:1C/ O1011001_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-A -17101 | 17FSL17101CV |  | DI-NIS (VFC) DCS |  | Сигнал | Low Flow Switch (Flow) | 4124-XZ-DM-21717101 | DCS_DI_01 | Field |  | 17-FSL-17101-CV | 01 Pair | Pr.01 | 17-MC-DCS-007 | TS-H-08 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate to Distribution Header | Сжиженный конденсат поступает в распределительный коллектор | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ACTIVE | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-08:1/ O1011114:12A | TS-H-08:2/ O1011114:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-A-020201B-PH | 17AT020201B-PH |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 30.05.2024 добавлен по TQ_ALL_051 | Сигнал | Analyzer |  | DCS_AI_01 |  |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.20 | 17-MC-DCS-006 | TS-O-02 | 39 | 40 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011000_U6 | HD5542 | O1011000 | TUA711-AIO16 | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | PH of water after cation exchange filters into the condensate tank pos. 17-T-031 | НЕКОНДИЦ КОНД ОТ P-030-A/B/C НА КАТИОНИТЫ | 17-AMMONIA UTILITIES | HOLD | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [9 empty] | 14 | [6 empty] | TS-O-02:39/ O1011000_U6:3 | TS-O-02:40/ O1011000_U6:4 |  |  | O1011000:6A/ O1011000_U6:5 | O1011000:6C/ O1011000_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17AT11301AC1 | 17AT11301AC1 |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 30.05.2024 добавлен по TQ_ALL_051 | Сигнал |  |  | DCS_AI_03 |  |  | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.10 | 17-MC-DCS-006 | TS-R-05 | 19 | 20 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U12 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | ДЫМОВЫЕ ГАЗЫ ПУСКОВОГО КОТЛА L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [8 empty] | 0 | 100 | [6 empty] | TS-R-05:19/ O1010007_U12:1 | TS-R-05:20/ O1010007_U12:2 |  |  | O1010007:12A/ O1010007_U12:5 | O1010007:12C/ O1010007_U12:6 | [6 empty] | 12A | 12C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17AT113650B | 17AT113650B |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 30.05.2024 добавлен по TQ_ALL_051 | Сигнал |  |  | DCS_AI_03 | Field |  | 17-C-AD-N-001-LP003-L111 | 12 Pair | Pr.07 | 17-MC-DCS-006 | TS-Q-08 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010006_U16 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Silica sampling | КОТЛОВАЯ ВОДА L-111-V-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 25 | ppb | [5 empty] | TS-Q-08:13/ O1010006_U16:1 | TS-Q-08:14/ O1010006_U16:2 |  |  | O1010006:16A/ O1010006_U16:5 | O1010006:16C/ O1010006_U16:6 | [6 empty] | 16A | 16C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 | 17AXS11301 | 17AXS11301 |  | DI-NIS (VFC) DCS | 30.05.2024 добавлен по TQ_ALL_051 | Сигнал |  |  | DCS_DI_01 |  |  | 17-C-DD-N-001FL11-AH001 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-F-18 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | 17-AH-001 СИСТЕМА НЕПРЕРЫВНОГО МОНИТОРИНГА ВЫБРОСОВ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | FAULT | NORMAL | [20 empty] | TS-F-18:5/ O1011114:15A | TS-F-18:6/ O1011114:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-B -113818 | 17BL113818X |  | DI-NIS (VFC) DCS |  | Сигнал | Status Indication | 4124-FB-VD-BD00317L11111372_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-008BL02 | 12 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-10 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | BRN - 1 - FUEL GAS - ON | ГОРЕЛКА 1 - РОЗЖИГ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | BMS | ON | OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-10:1/ O1011113:12A | TS-F-10:2/ O1011113:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-B -113828 | 17BL113828X |  | DI-NIS (VFC) DCS |  | Сигнал | Status Indication | 4124-FB-VD-BD00317L11111372_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-008BL02 | 12 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-10 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | BRN - 2 - FUEL GAS - ON | ГОРЕЛКА 2 - РОЗЖИГ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | BMS | ON | OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-10:3/ O1011113:13A | TS-F-10:4/ O1011113:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-B -113838 | 17BL113838X |  | DI-NIS (VFC) DCS |  | Сигнал | Status Indication | 4124-FB-VD-BD00317L11111372_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-008BL02 | 12 Pair | Pr.03 | 17-MC-DCS-007 | TS-F-10 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | BRN - 3 - FUEL GAS - ON | ГОРЕЛКА 3 - РОЗЖИГ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | BMS | ON | OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-10:5/ O1011113:14A | TS-F-10:6/ O1011113:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-B -113848 | 17BL113848X |  | DI-NIS (VFC) DCS |  | Сигнал | Status Indication | 4124-FB-VD-BD00317L11111372_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-008BL02 | 12 Pair | Pr.04 | 17-MC-DCS-007 | TS-F-10 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | BRN -4 - FUEL GAS - ON | ГОРЕЛКА 4 - РОЗЖИГ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | BMS | ON | OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-10:7/ O1011113:15A | TS-F-10:8/ O1011113:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-E -111 | 17XSE111 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Running status | 4124-XZ-DM-21711801 | DCS_DI_03 | Thristor Contol panel |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.09 | 17-MC-DCS-003 | TS-H-01 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-111 Fuel Gas Electrical heater | ЭЛ.НАГРЕВАТЕЛЬ ПРИР ГАЗА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:17/ O1010208:16A | TS-H-01:18/ O1010208:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-E -111 | 17XSAE111 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Electric Heater available status | 4124-XZ-DM-21711801 | DCS_DI_03 | Thristor Contol panel |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.10 | 17-MC-DCS-003 | TS-H-01 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-111 Fuel Gas Electrical heater | 17E111 ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:19/ O1010208:17A | TS-H-01:20/ O1010208:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-E -111 | 17XSRE111 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Remote status | 4124-XZ-DM-21711801 | DCS_DI_03 | Thristor Contol panel |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.11 | 17-MC-DCS-003 | TS-H-01 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-111 Fuel Gas Electrical heater | 17E111 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:21/ O1010208:18A | TS-H-01:22/ O1010208:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-E -111 | 17XYSPE111 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-XZ-DM-21711801 | DCS_DO_03 | Thristor Contol panel |  | 17-I-CD-N-020BL02 | 16 Core | C.01 | 17-MC-DCS-003 | TS-F-01 | 1 | 2 |  | 16 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-111 Fuel Gas Electrical heater | 17E111 ПУСК | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-F-01:2/ O1010214:31A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-E -111 | 17XYSTE111 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-XZ-DM-21711801 | DCS_DO_03 | Thristor Contol panel |  | 17-I-CD-N-020BL02 | 16 Core | C.03 | 17-MC-DCS-003 | TS-F-01 | 3 | 4 |  | 16 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-111 Fuel Gas Electrical heater | 17E111 СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-F-01:4/ O1010214:32A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -00005 | 17FT00005 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Conductivity Analyzer Transmitter | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.04 | 17-MC-DCS-009 | TS-H-03 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U1 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP steam to Dearetor | ПАР НД В ДЕАЭРАТОР | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 48000 | kg/h | [5 empty] | TS-H-03:7/ O1011006_U1:3 | TS-H-03:8/ O1011006_U1:4 |  |  | O1011006:1A/ O1011006_U1:5 | O1011006:1C/ O1011006_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -020200 -A | 17FT020200A |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.03 | 17-MC-DCS-008 | TS-O-01 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U1 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet SAC Cationic Exchanger | ВХОД В КАТИОНИТ S-021А | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 15 | 320 |  | 0 | 450 | m³/h | [5 empty] | TS-O-01:5/ O1011010R_U1:3 | TS-O-01:6/ O1011010R_U1:4 |  |  | O1011010R:1A/ O1011010R_U1:5 | O1011010R:1C/ O1011010R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -020200 -A | 17FY020200A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.04 | 17-MC-DCS-008 | TS-O-01 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U1 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 1 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet SAC Cationic Exchanger | ВХОД КАТИОНООБМЕННИКА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-O-01:7/ O1011014R_U1:3 | TS-O-01:8/ O1011014R_U1:4 |  |  | O1011014R:1A/ O1011014R_U1:5 | O1011014R:1C/ O1011014R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -020200 -B | 17FT020200B |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.08 | 17-MC-DCS-008 | TS-O-01 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U2 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet SAC Cationic Exchanger | ВХОД В КАТИОНИТ S-021В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 15 | 320 |  | 0 | 450 | m³/h | [5 empty] | TS-O-01:15/ O1011010R_U2:3 | TS-O-01:16/ O1011010R_U2:4 |  |  | O1011010R:2A/ O1011010R_U2:5 | O1011010R:2C/ O1011010R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -020200 -B | 17FY020200B |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.09 | 17-MC-DCS-008 | TS-O-01 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U2 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 2 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet SAC Cationic Exchanger | ВХОД КАТИОНООБМЕННИКА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-O-01:17/ O1011014R_U2:3 | TS-O-01:18/ O1011014R_U2:4 |  |  | O1011014R:2A/ O1011014R_U2:5 | O1011014R:2C/ O1011014R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -020200 -C | 17FT020200C |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.13 | 17-MC-DCS-008 | TS-O-01 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U3 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet SAC Cationic Exchanger | ВХОД В КАТИОНИТ S-021С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 15 | 320 |  | 0 | 450 | m³/h | [5 empty] | TS-O-01:25/ O1011010R_U3:3 | TS-O-01:26/ O1011010R_U3:4 |  |  | O1011010R:3A/ O1011010R_U3:5 | O1011010R:3C/ O1011010R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -020200 -C | 17FY020200C |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.14 | 17-MC-DCS-008 | TS-O-01 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U3 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 3 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet SAC Cationic Exchanger | ВХОД КАТИОНООБМЕННИКА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-O-01:27/ O1011014R_U3:3 | TS-O-01:28/ O1011014R_U3:4 |  |  | O1011014R:3A/ O1011014R_U3:5 | O1011014R:3C/ O1011014R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -020201 -A | 17FT020201A |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_02 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.02 | 17-MC-DCS-008 | TS-O-03 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U7 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet Mixed bed | ВХОД В ФСД S-022А | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 15 | 350 |  | 0 | 450 | m³/h | [5 empty] | TS-O-03:3/ O1011010R_U7:3 | TS-O-03:4/ O1011010R_U7:4 |  |  | O1011010R:7A/ O1011010R_U7:5 | O1011010R:7C/ O1011010R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -020201 -A | 17FY020201A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.03 | 17-MC-DCS-008 | TS-O-03 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U7 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 7 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet Mixed bed | ВХОД СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-O-03:5/ O1011014R_U7:3 | TS-O-03:6/ O1011014R_U7:4 |  |  | O1011014R:7A/ O1011014R_U7:5 | O1011014R:7C/ O1011014R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -020201 -B | 17FT020201B |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_02 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.07 | 17-MC-DCS-008 | TS-O-03 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U8 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet Mixed bed | ВХОД В ФСД S-022В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 15 | 350 |  | 0 | 450 | m³/h | [5 empty] | TS-O-03:13/ O1011010R_U8:3 | TS-O-03:14/ O1011010R_U8:4 |  |  | O1011010R:8A/ O1011010R_U8:5 | O1011010R:8C/ O1011010R_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -020201 -B | 17FY020201B |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.08 | 17-MC-DCS-008 | TS-O-03 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U8 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 8 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet Mixed bed | ВХОД СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-O-03:15/ O1011014R_U8:3 | TS-O-03:16/ O1011014R_U8:4 |  |  | O1011014R:8A/ O1011014R_U8:5 | O1011014R:8C/ O1011014R_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -020201 -C | 17FT020201C |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_02 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.12 | 17-MC-DCS-008 | TS-O-03 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U9 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet Mixed bed | ВХОД В ФСД S-022С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 15 | 350 |  | 0 | 450 | m³/h | [5 empty] | TS-O-03:23/ O1011010R_U9:3 | TS-O-03:24/ O1011010R_U9:4 |  |  | O1011010R:9A/ O1011010R_U9:5 | O1011010R:9C/ O1011010R_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -020201 -C | 17FY020201C |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.13 | 17-MC-DCS-008 | TS-O-03 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U9 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 9 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inlet Mixed bed | ВХОД СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-O-03:25/ O1011014R_U9:3 | TS-O-03:26/ O1011014R_U9:4 |  |  | O1011014R:9A/ O1011014R_U9:5 | O1011014R:9C/ O1011014R_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -020202 | 17FT020202 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_AI_02 | Field |  | 17-C-AD-N-003FL03-L022 | 12 Pair | Pr.04 | 17-MC-DCS-008 | TS-O-06 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011010R_U12 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Water from regeneration pumps | ДЕМ ВОДА ОТ P-033А/В/С НА РЕГЕНЕРАЦИЮ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 15 | 30 |  | 0 | 100 | m³/h | [5 empty] | TS-O-06:7/ O1011010R_U12:3 | TS-O-06:8/ O1011010R_U12:4 |  |  | O1011010R:12A/ O1011010R_U12:5 | O1011010R:12C/ O1011010R_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -020202 | 17FY020202 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL03-L022 | 12 Pair | Pr.05 | 17-MC-DCS-008 | TS-O-06 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011014R_U11 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 11 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Water from regeneration pumps | ВОДА ИЗ НАСОСА РЕГЕНЕРАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-O-06:9/ O1011014R_U11:3 | TS-O-06:10/ O1011014R_U11:4 |  |  | O1011014R:11A/ O1011014R_U11:5 | O1011014R:11C/ O1011014R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -020203 | 17FT020203 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_AI_02 | Field |  | 17-C-AD-N-003FL03-L022 | 12 Pair | Pr.06 | 17-MC-DCS-008 | TS-O-06 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011010R_U13 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Water to NaOH regeneration | ДЕМ ВОДА ОТ P-033А/В/С НА РЕГЕНЕРАЦИЮ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 28 |  | 0 | 40 | m³/h | [5 empty] | TS-O-06:11/ O1011010R_U13:3 | TS-O-06:12/ O1011010R_U13:4 |  |  | O1011010R:13A/ O1011010R_U13:5 | O1011010R:13C/ O1011010R_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -020203 | 17FY020203 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL03-L022 | 12 Pair | Pr.07 | 17-MC-DCS-008 | TS-O-06 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011014R_U12 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 12 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Water to NaOH regeneration | ВОДА К РЕГЕНЕРАЦИИ NAOH | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-O-06:13/ O1011014R_U12:3 | TS-O-06:14/ O1011014R_U12:4 |  |  | O1011014R:12A/ O1011014R_U12:5 | O1011014R:12C/ O1011014R_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -020204 | 17FT020204 |  | AI-R-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Magnetic Flow Transmitter | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_AI_04 | Field | 230 VAC | 17-C-AD-N-006FL03-L022 | 24 Pair | Pr.01 | 17-MC-DCS-008 | TS-P-03 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U14 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Neutralized water to plant drain system | РЕГЕНЕРАЦИОННЫЕ СТОКИ НА ВОДОПОДГОТОВКУ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 28 |  | 0 | 40 | m³/h | [5 empty] | TS-P-03:1/ O1011010R_U14:1 | TS-P-03:2/ O1011010R_U14:2 |  |  | O1011010R:14A/ O1011010R_U14:5 | O1011010R:14C/ O1011010R_U14:6 | [6 empty] | 14A | 14C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -020204 | 17FY020204 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_AO_02 | Field |  | 17-C-AD-N-006FL03-L022 | 24 Pair | Pr.02 | 17-MC-DCS-008 | TS-P-03 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U15 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 15 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Neutralized water to plant drain system | НЕЙТРАЛ.ВОДА В ДРЕН.СИСТЕМУ ЗАВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-P-03:3/ O1011014R_U15:3 | TS-P-03:4/ O1011014R_U15:4 |  |  | O1011014R:15A/ O1011014R_U15:5 | O1011014R:15C/ O1011014R_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -02089 | 17FT02089 |  | AI-NIS (4-20 mA, 4 wire) DCS |  | Сигнал | Magnetic Flow Transmitter | 4124-XZ-DM-21702020 | DCS_AI_03 | Field | 230 VAC | 17-C-AD-N-003FL10 | 24 Pair | Pr.06 | 17-MC-DCS-006 | TS-Q-04 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010000_U9 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 9 | AI713-H11 | 16 |  | 16.02.2024 добавлен Loop_External_power |  | DCS AMMONIA-UTILITIES | 17-P-021 discharge to process condensate stripper | НЕКОН КОНДЕНСАТ ИЗ Т-021 В 130-D | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 14400 |  |  | 0 | 25000 | kg/h | [5 empty] | TS-Q-04:11/ O1010000_U9:1 | TS-Q-04:12/ O1010000_U9:2 |  |  | O1010000:9A/ O1010000_U9:5 | O1010000:9C/ O1010000_U9:6 | [6 empty] | 9A | 9C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -03005 | 17FT03005 |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21703001 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.01 | 17-MC-DCS-006 | TS-O-02 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U11 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 17-P-032 A/B/C discharge line | ДЕМ ВОДА ОТ 17-P-032 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 315000 |  |  | 0 | 1100000 | kg/h | [5 empty] | TS-O-02:1/ O1010012R_U11:3 | TS-O-02:2/ O1010012R_U11:4 |  |  | O1010012R:11A/ O1010012R_U11:5 | O1010012R:11C/ O1010012R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -03005 | 17FY03005 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21703001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.02 | 17-MC-DCS-006 | TS-O-02 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U11 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 11 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 7-P-032A/B/C discharge line | ДЕМ ВОДА НА НАГНЕТАНИИ 17P032 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-02:3/ O1010104R_U11:3 | TS-O-02:4/ O1010104R_U11:4 |  |  | O1010104R:11A/ O1010104R_U11:5 | O1010104R:11C/ O1010104R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -03010 | 17FT03010 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.01 | 17-MC-DCS-006 | TS-Q-05 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U9 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Urea Melt Steam Condensate to 17-T-030 | ПАРОВЫЙ КОНД С КАРБАМИДА В Т-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 115000 | kg/h | [5 empty] | TS-Q-05:1/ O1010005_U9:3 | TS-Q-05:2/ O1010005_U9:4 |  |  | O1010005:9A/ O1010005_U9:5 | O1010005:9C/ O1010005_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -03021 | 17FT03021 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.07 | 17-MC-DCS-006 | TS-Q-04 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U3 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate from NH3 plant to 17-T-030 | ТУРБИННЫЙ КОНД В T-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 295800 | kg/h | [5 empty] | TS-Q-04:13/ O1010005_U3:3 | TS-Q-04:14/ O1010005_U3:4 |  |  | O1010005:3A/ O1010005_U3:5 | O1010005:3C/ O1010005_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -03022 | 17FT03022 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.02 | 17-MC-DCS-006 | TS-Q-05 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U10 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate from CO2 Comp to 17-T-030 | ТУРБ КОНД ОТ КОМПР СО2 В T-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 200000 | kg/h | [5 empty] | TS-Q-05:3/ O1010005_U10:3 | TS-Q-05:4/ O1010005_U10:4 |  |  | O1010005:10A/ O1010005_U10:5 | O1010005:10C/ O1010005_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -03023 | 17FT03023 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.03 | 17-MC-DCS-006 | TS-Q-05 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U11 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Process Condensate from Ammonia plant to 17-T-030 | ОТПАРНОЙ КОНД В T-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 155000 | kg/h | [5 empty] | TS-Q-05:5/ O1010005_U11:3 | TS-Q-05:6/ O1010005_U11:4 |  |  | O1010005:11A/ O1010005_U11:5 | O1010005:11C/ O1010005_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -03024 | 17FT03024 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.04 | 17-MC-DCS-006 | TS-Q-05 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U12 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Process Condensate from Urea plant to 17-T-030 | ТЕХН КОНД ПЛАВА КАРБАМИДА T-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 80000 | kg/h | [5 empty] | TS-Q-05:7/ O1010005_U12:3 | TS-Q-05:8/ O1010005_U12:4 |  |  | O1010005:12A/ O1010005_U12:5 | O1010005:12C/ O1010005_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -03025 | 17FT03025 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21703004 | DCS_AI_02 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.08 | 17-MC-DCS-006 | TS-Q-04 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U7 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Process Condensate from 17-P-030 A/B/C | КОНД ОТ 030-A/B/C НА КАТИОНИТЫ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 121500 |  |  | 0 | 700000 | kg/h | [5 empty] | TS-Q-04:15/ O1010014R_U7:3 | TS-Q-04:16/ O1010014R_U7:4 |  |  | O1010014R:7A/ O1010014R_U7:5 | O1010014R:7C/ O1010014R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -03025 | 17FY03025 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21703004 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.10 | 17-MC-DCS-006 | TS-Q-04 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010106R_U5 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 5 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Process Condensate from 17-P-030 A/B/C | ТЕХНОЛ КОНДЕНСАТ ОТ 17P030A/B/C | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:19/ O1010106R_U5:3 | TS-Q-04:20/ O1010106R_U5:4 |  |  | O1010106R:5A/ O1010106R_U5:5 | O1010106R:5C/ O1010106R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -03062 | 17FT03062 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21703003 | DCS_AI_02 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.09 | 17-MC-DCS-006 | TS-Q-04 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U8 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-031A/B/C discharge to 17-S-022A/B/C | ТЕХНОЛ КОНД ОТ Т-031 НА ФСД | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 243000 |  |  | 0 | 795410 | kg/h | [5 empty] | TS-Q-04:17/ O1010014R_U8:3 | TS-Q-04:18/ O1010014R_U8:4 |  |  | O1010014R:8A/ O1010014R_U8:5 | O1010014R:8C/ O1010014R_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -03062 | 17FY03062 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21703003 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.11 | 17-MC-DCS-006 | TS-Q-04 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010106R_U6 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 6 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-031A/B/C discharge to 17-S-022A/B/C | ТЕХНОЛ КОНДЕНСАТ НА 17-L-022 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:21/ O1010106R_U6:3 | TS-Q-04:22/ O1010106R_U6:4 |  |  | O1010106R:6A/ O1010106R_U6:5 | O1010106R:6C/ O1010106R_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -07003 | 17FT07003 |  | AI-R-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Magnetic Flow Transmitter | 4124-XZ-DM-21707001 | DCS_AI_04 | Field | 230 VAC | 17-C-AD-N-002FL07 | 24 Pair | Pr.16 | 17-MC-DCS-006 | TS-Q-03 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U6 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 6 | AI713-H11 | 16 |  | 16.02.2024 добавлен Loop_External_power |  | DCS AMMONIA-UTILITIES | Cooling water blowdown header | ПРОДУВКА ВОЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 138000 | 278000 |  | 0 | 910000 | kg/h | [5 empty] | TS-Q-03:31/ O1010014R_U6:1 | TS-Q-03:32/ O1010014R_U6:2 |  |  | O1010014R:6A/ O1010014R_U6:5 | O1010014R:6C/ O1010014R_U6:6 | [6 empty] | 6A | 6C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -07021 | 17FT07021 |  | AI-R-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Magnetic Flow Transmitter | 4124-XZ-DM-21707002 | DCS_AI_04 | Field | 230 VAC | 17-C-AD-N-002FL07 | 24 Pair | Pr.05 | 17-MC-DCS-006 | TS-Q-03 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U4 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 4 | AI713-H11 | 16 |  | 16.02.2024 добавлен Loop_External_power |  | DCS AMMONIA-UTILITIES | Cooling water to 17-L-072 | ОВ НА ФИЛЬТРАЦИЮ L-072А/В | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 456130 | 1600000 |  | 0 | 2150000 | kg/h | [5 empty] | TS-Q-03:9/ O1010014R_U4:1 | TS-Q-03:10/ O1010014R_U4:2 |  |  | O1010014R:4A/ O1010014R_U4:5 | O1010014R:4C/ O1010014R_U4:6 | [6 empty] | 4A | 4C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -07021 | 17FY07021 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21707002 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.02 | 17-MC-DCS-006 | TS-Q-03 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010106R_U4 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 4 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Discharge Header from 17-P-071A-G | ОХЛ ВОДА ОТ НАСОСОВ 17-P-071A-G | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:3/ O1010106R_U4:3 | TS-Q-03:4/ O1010106R_U4:4 |  |  | O1010106R:4A/ O1010106R_U4:5 | O1010106R:4C/ O1010106R_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -07053 | 17FT07053 |  | AI-NIS (4-20 mA, 4 wire) DCS |  | Сигнал | Magnetic Flow Transmitter | 4124-XZ-DM-21707007 | DCS_AI_03 | Field | 230 VAC | 17-C-AD-N-002FL07 | 24 Pair | Pr.03 | 17-MC-DCS-006 | TS-Q-03 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U2 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 2 | AI713-H11 | 16 |  | 16.02.2024 добавлен Loop_External_power |  | DCS AMMONIA-UTILITIES | Pump 17-P-073 AB discharge to distribution header | АВАР ОХЛ ВОДА В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 910000 | kg/h | [5 empty] | TS-Q-03:5/ O1010006_U2:1 | TS-Q-03:6/ O1010006_U2:2 |  |  | O1010006:2A/ O1010006_U2:5 | O1010006:2C/ O1010006_U2:6 | [6 empty] | 2A | 2C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -07055 | 17FT07055 |  | AI-R-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Magnetic Flow Transmitter | 4124-XZ-DM-21707003 | DCS_AI_04 | Field | 230 VAC | 17-C-AD-N-002FL07 | 24 Pair | Pr.04 | 17-MC-DCS-006 | TS-Q-03 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U3 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 3 | AI713-H11 | 16 |  | 16.02.2024 добавлен Loop_External_power |  | DCS AMMONIA-UTILITIES | Service water for Cooling Tower make-up | ПОДПИТКА ГРАДИРНИ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 970000 | kg/h | [5 empty] | TS-Q-03:7/ O1010014R_U3:1 | TS-Q-03:8/ O1010014R_U3:2 |  |  | O1010014R:3A/ O1010014R_U3:5 | O1010014R:3C/ O1010014R_U3:6 | [6 empty] | 3A | 3C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -09001 | 17FT09001 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21709001 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL10 | 12 Pair | Pr.01 | 17-MC-DCS-009 | TS-G-01 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U1 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Plant Air from 17-L-091 | ТЕХНИЧЕСКИЙ ВОЗДУХ В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 50 | 656.4 |  | 0 | 71.43 | m3/h | [5 empty] | TS-G-01:1/ O1010011_U1:3 | TS-G-01:2/ O1010011_U1:4 |  |  | O1010011:1A/ O1010011_U1:5 | O1010011:1C/ O1010011_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -09031 | 17FT09031 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21709002 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL10 | 12 Pair | Pr.02 | 17-MC-DCS-009 | TS-G-01 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U2 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | To Instrument Air header | ВОЗДУХ КИП В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 1644 |  | 0 | 256.96 | m3/h | [5 empty] | TS-G-01:3/ O1010011_U2:3 | TS-G-01:4/ O1010011_U2:4 |  |  | O1010011:2A/ O1010011_U2:5 | O1010011:2C/ O1010011_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -10001 | 17FT10001 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21710001 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.01 | 17-MC-DCS-008 | TS-P-01 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010009_U1 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | АЗОТ ИЗ 17-V-106 В СЕТЬ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 313.2 | m3/h | [5 empty] | TS-P-01:1/ O1010009_U1:3 | TS-P-01:2/ O1010009_U1:4 |  |  | O1010009:1A/ O1010009_U1:5 | O1010009:1C/ O1010009_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -10002 | 17FT10002 |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21710001 | DCS_AI_02 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.02 | 17-MC-DCS-008 | TS-P-01 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010100R_U1 | HD5542 | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Low pressure nitrogen to Owner BL | АЗОТ НД НА ГРАНИЦЫ УСТАНОВКИ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 675 | 2625 |  | 0 | 311.89 | m3/h | [5 empty] | TS-P-01:3/ O1010100R_U1:3 | TS-P-01:4/ O1010100R_U1:4 |  |  | O1010100R:1A/ O1010100R_U1:5 | O1010100R:1C/ O1010100R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -10002 | 17FY10002 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21710001 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.03 | 17-MC-DCS-008 | TS-P-01 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010108R_U1 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 1 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | АЗОТ ИЗ V-103/106 СЕТЬ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-01:5/ O1010108R_U1:3 | TS-P-01:6/ O1010108R_U1:4 |  |  | O1010108R:1A/ O1010108R_U1:5 | O1010108R:1C/ O1010108R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 | 17-F -11301 | 17FT11301 |  | AI-NIS (4-20 mA, 4 wire) DCS | 30.05.2024 изм тип сигнала на актив | Сигнал | DP Flow Transmitter (Flow) | 4124-XZ-DM-21711301 | DCS_AI_03 | Field | 230VAC | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.07 | 17-MC-DCS-006 | TS-R-05 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U7 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 7 | AI713-H11 | 16 |  |  | 25 Вт | DCS AMMONIA-UTILITIES | CEMS for Star-Up-Boiler 17-L-111 | РАСХОД ДЫМОВЫХ ГАЗОВ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | CEMS |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 115000 | 360000 |  | 0 | 60.69 | kg/s | [5 empty] | TS-R-05:13/ O1010007_U7:1 | TS-R-05:14/ O1010007_U7:2 |  |  | O1010007:7A/ O1010007_U7:5 | O1010007:7C/ O1010007_U7:6 | [6 empty] | 7A | 7C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -113500 | 17FT113500 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Flow Transmitter | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.01 | 17-MC-DCS-006 | TS-O-05 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U16 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | FROM FW PUMPS 17-P-111A/B | ОТ НАСОСОВ КОТЛ ВОДЫ P-111A/B | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 310000 | kg/h | [5 empty] | TS-O-05:1/ O1010012R_U16:3 | TS-O-05:2/ O1010012R_U16:4 |  |  | O1010012R:16A/ O1010012R_U16:5 | O1010012R:16C/ O1010012R_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -113501 | 17FT113501 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Flow Transmitter | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.17 | 17-MC-DCS-008 | TS-P-02 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010010_U6 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | ПАР СД ОТ КОТЛА В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 310000 | kg/h | [5 empty] | TS-P-02:33/ O1010010_U6:3 | TS-P-02:34/ O1010010_U6:4 |  |  | O1010010:6A/ O1010010_U6:5 | O1010010:6C/ O1010010_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -113502 | 17FT113502 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Flow Transmitter | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.02 | 17-MC-DCS-006 | TS-O-05 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010003_U13 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM DRUM LEVEL | КОТЛОВАЯ ВОДА НА ПАРОПЕРЕГРЕВ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 28700 | kg/h | [5 empty] | TS-O-05:3/ O1010003_U13:3 | TS-O-05:4/ O1010003_U13:4 |  |  | O1010003:13A/ O1010003_U13:5 | O1010003:13C/ O1010003_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -113520 | 17FT113520 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Flow Transmitter | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.18 | 17-MC-DCS-008 | TS-P-02 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010010_U7 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | AIR DUCT VENTURI FLOW | ВОЗДУХ НА ГОРЕНИЕ ПУСКОВОГО КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 352700 | kg/h | [5 empty] | TS-P-02:35/ O1010010_U7:3 | TS-P-02:36/ O1010010_U7:4 |  |  | O1010010:7A/ O1010010_U7:5 | O1010010:7C/ O1010010_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113520 -A | 17FY113520A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FB-VD-BD00317L11111303 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.11 | 17-MC-DCS-008 | TS-P-02 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010108R_U4 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 4 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | ПАР ТУРБИНЫ 17-L-111-STK-101-A | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-02:21/ O1010108R_U4:3 | TS-P-02:22/ O1010108R_U4:4 |  |  | O1010108R:4A/ O1010108R_U4:5 | O1010108R:4C/ O1010108R_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113520 -A | 17FZSL113520A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FB-VD-BD00317L11111303 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL11-L111 | 06 Pair | Pr.03 | 17-MC-DCS-001 | TS-G-06 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010203_U6 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | ПАР ТУРБИНЫ 17-L-111-STK-101-A | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-06:5/ O1010203_U6:3 | TS-G-06:6/ O1010203_U6:4 |  |  | O1010203:6A/ O1010203_U6:5 | O1010203:6B/ O1010203_U6:6 | [6 empty] | 6A | 6B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113520 -B | 17AT113500 |  | AI-NIS (4-20 mA, 4 wire) DCS |  | Сигнал | O2 Analyzer Transmitter | 4124-FB-VD-BD00317L11111303 | DCS_AI_03 | Field | 230 VAC | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.05 | 17-MC-DCS-008 | TS-P-02 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010010_U2 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CASING OXIGEN ANALYZER | КИСЛОРОД В КОНВЕКЦ ЗОНЕ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0.0 | 25.0 | % | [5 empty] | TS-P-02:9/ O1010010_U2:1 | TS-P-02:10/ O1010010_U2:2 |  |  | O1010010:2A/ O1010010_U2:5 | O1010010:2C/ O1010010_U2:6 | [6 empty] | 2A | 2C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113520 -B | 17FY113520B |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FB-VD-BD00317L11111303 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.12 | 17-MC-DCS-008 | TS-P-02 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010108R_U5 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 5 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | ВЕНТИЛЯТОР КОТЛА 17-L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-02:23/ O1010108R_U5:3 | TS-P-02:24/ O1010108R_U5:4 |  |  | O1010108R:5A/ O1010108R_U5:5 | O1010108R:5C/ O1010108R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113520 -B | 17FZSL113520B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FB-VD-BD00317L11111303 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL11-L111 | 06 Pair | Pr.04 | 17-MC-DCS-001 | TS-G-06 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010203_U7 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | ВЕНТИЛЯТОР КОТЛА 17-L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-06:7/ O1010203_U7:3 | TS-G-06:8/ O1010203_U7:4 |  |  | O1010203:7A/ O1010203_U7:5 | O1010203:7B/ O1010203_U7:6 | [6 empty] | 7A | 7B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -113530 | 17FT113530 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Flow Transmitter | 4124-FB-VD-BD00317L11111341 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.08 | 17-MC-DCS-008 | TS-P-02 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010010_U5 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | MP STEAM FROM DISTRIBUTION | ПАР СД НА ТУРБИНУ 17-L-111-STK-101A | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 14000 | kg/h | [5 empty] | TS-P-02:15/ O1010010_U5:3 | TS-P-02:16/ O1010010_U5:4 |  |  | O1010010:5A/ O1010010_U5:5 | O1010010:5C/ O1010010_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113622 | 17FSL113622 |  | DI-NIS (VFC) DCS |  | Сигнал | Low Flow Switch | 4124-FB-VD-BD00317L11111388 | DCS_DI_01 | Field |  | 17-C-DD-N-001-LP003-L111 | 12 Pair | Pr.04 | 17-MC-DCS-001 | TS-F-04 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From Strainer 17-L-111-S-140 | ПРОБА КРЕМНЕЗЕМА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:7/ O1010200:21A | TS-F-04:8/ O1010200:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113623 | 17FSL113623 |  | DI-NIS (VFC) DCS |  | Сигнал | Low Flow Switch | 4124-FB-VD-BD00317L11111388 | DCS_DI_01 | Field |  | 17-C-DD-N-001-LP003-L111 | 12 Pair | Pr.05 | 17-MC-DCS-001 | TS-F-04 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From Strainer 17-L-111-S-141 | ИЗ ФИЛЬТРА 17-L-111-S-141 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:9/ O1010200:22A | TS-F-04:10/ O1010200:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113624 | 17FSL113624 |  | DI-NIS (VFC) DCS |  | Сигнал | Low Flow Switch | 4124-FB-VD-BD00317L11111388 | DCS_DI_01 | Field |  | 17-C-DD-N-001-LP003-L111 | 12 Pair | Pr.06 | 17-MC-DCS-001 | TS-F-04 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From Strainer 17-L-111-S-142 | ИЗ ФИЛЬТРА 17-L-111-S-142 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:11/ O1010200:23A | TS-F-04:12/ O1010200:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -113801 | 17FT113801 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Position Open Proximity Switch | 4124-FB-VD-BD00317L11111372_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-I-001FL11-L111 | 24 Pair | Pr.06 | 17-MC-DCS-009 | TS-H-04 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010102R_U10 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO ATMOSPHERE | ТГ НА ГОРЕЛКИ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 19000 | kg/h | [5 empty] | TS-H-04:11/ O1010102R_U10:3 | TS-H-04:12/ O1010102R_U10:4 |  |  | O1010102R:10A/ O1010102R_U10:5 | O1010102R:10C/ O1010102R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113801 | 17FY113801 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FB-VD-BD00317L11111372_SH.1 | DCS_AO_02 | Field |  | 17-C-AD-I-001FL11-L111 | 24 Pair | Pr.10 | 17-MC-DCS-009 | TS-H-04 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010110R_U15 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 15 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO ATMOSPHERE | В АТМОСФЕРУ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-H-04:19/ O1010110R_U15:3 | TS-H-04:20/ O1010110R_U15:4 |  |  | O1010110R:15A/ O1010110R_U15:5 | O1010110R:15C/ O1010110R_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -113802 | 17FY113802 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FB-VD-BD00317L11111372_SH.1 | DCS_AO_02 | Field |  | 17-C-AD-I-001FL11-L111 | 24 Pair | Pr.11 | 17-MC-DCS-009 | TS-H-04 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010110R_U11 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 11 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO ATMOSPHERE | В АТМОСФЕРУ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-H-04:21/ O1010110R_U11:3 | TS-H-04:22/ O1010110R_U11:4 |  |  | O1010110R:11A/ O1010110R_U11:5 | O1010110R:11C/ O1010110R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -11700 | 17FT11700 |  | AI-R-IS (4-20 mA, 4 wire) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21711701 | DCS_AI_04 | Field | 230 VAC | 17-C-AD-I-001FL11 | 24 Pair | Pr.06 | 17-MC-DCS-009 | TS-H-03 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010102R_U6 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 6 | AI713-H11 | 16 |  | 16.02.2024 добавлен Loop_External_power |  | DCS AMMONIA-UTILITIES | Blowdown from Start-up Boiler 17-L-111 | ПРОДУВКА КОТЛА В 17-V-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 12000 | kg/h | [5 empty] | TS-H-03:11/ O1010102R_U6:1 | TS-H-03:12/ O1010102R_U6:2 |  |  | O1010102R:6A/ O1010102R_U6:5 | O1010102R:6C/ O1010102R_U6:6 | [6 empty] | 6A | 6C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -11700 | 17FY11700 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21711701 | DCS_AO_02 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.07 | 17-MC-DCS-009 | TS-H-03 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010110R_U6 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 6 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Blowdown from Start-up Boiler 17-L-111 | ПРОДУВКИ ИЗ 17-L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-H-03:13/ O1010110R_U6:3 | TS-H-03:14/ O1010110R_U6:4 |  |  | O1010110R:6A/ O1010110R_U6:5 | O1010110R:6C/ O1010110R_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -11801 | 17FT11801 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Flow Transmitter | 4124-XZ-DM-21711801 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11 | 12 Pair | Pr.10 | 17-MC-DCS-006 | TS-O-04 | 19 | 20 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010003_U12 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Fuel gas to Distribution | ТГ НА ГОРЕЛКИ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 22000 | kg/h | [5 empty] | TS-O-04:19/ O1010003_U12:3 | TS-O-04:20/ O1010003_U12:4 |  |  | O1010003:12A/ O1010003_U12:5 | O1010003:12C/ O1010003_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F -17101 | 17FT17101 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21717101 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.02 | 17-MC-DCS-008 | TS-O-02 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011001_U2 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Hot Glycol Water supply to Distribution | ГЛИКОЛИВАЯ ВОДА В СЕТЬ | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 280800 | 365000 |  | 0 | 460000 | kg/h | [5 empty] | TS-O-02:3/ O1011001_U2:3 | TS-O-02:4/ O1011001_U2:4 |  |  | O1011001:2A/ O1011001_U2:5 | O1011001:2C/ O1011001_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-F -17102 | 17FT17102 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Vortex Flow Transmitter | 4124-XZ-DM-21717101 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.03 | 17-MC-DCS-008 | TS-O-02 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011001_U3 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 17-P-172 Discharge line | ЛИНИЯ НАГНЕТАНИЯ 17-P-172 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 7700 | kg/h | [5 empty] | TS-O-02:5/ O1011001_U3:3 | TS-O-02:6/ O1011001_U3:4 |  |  | O1011001:3A/ O1011001_U3:5 | O1011001:3C/ O1011001_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F-3002 | 17FT3002 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter |  | DCS_AI_01 | Field |  | 17-С-AD-I-1-FL90 | 15 Pair | Pr.07 | 17-MC-DCS-009 | TS-H-05 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A | O1011005_U1 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | HHP nitrogen consumption in the pipeline from Ammonia-2 to Urea | АЗОТ СВД ОТ АММИАКА-2 НА КАРБАМИД | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 4000 | s.m3/h | [5 empty] | TS-H-05:13/ O1011005_U1:3 | TS-H-05:14/ O1011005_U1:4 |  |  | O1011005:1A/ O1011005_U1:5 | O1011005:1C/ O1011005_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F-3003 | 17FT3003 |  | AI-NIS (4-20 mA, 4 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 30.05.2024 добавлено питание 24 | Сигнал | Thermal Mass Flow Meter |  | DCS_AI_03 | Field | 24VDC | 17-С-AD-N-1-FL90 | 05 Pair | Pr.01 | 17-MC-DCS-008 | TS-P-06 | 1 | 2 |  | 10 | AVK 2,5 A, AVK 2,5 A | O1010010_U8 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP carbon dioxide consumption in the Ammonia-1 and 2 pipeline to Urea | СО2 НД ОТ АММИАКА-2 НА КАРБАМИД | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 139500 | kg/h | [5 empty] | TS-P-06:1/ O1010010_U8:1 | TS-P-06:2/ O1010010_U8:2 |  |  | O1010010:8A/ O1010010_U8:5 | O1010010:8C/ O1010010_U8:6 | [6 empty] | 8A | 8C | 1 | 2 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F-3003 | 17FT3003 |  | Питание | 07.04.25 изм TAG_SERVICE_RU по TQ-131 30.05.2024 добавлено | Сигнал | Thermal Mass Flow Meter |  |  | Field | 24VDC | 17-С-AD-N-1-FL90 | 05 Pair | Pr.02 | 17-MC-DCS-008 | TS-P-06 | 3 | 4 |  | 10 | AVK 2,5 A, AVK 2,5 A |  |  | 0 |  | // 17-MC-DCS-008 | [10 empty] | 13 Вт |  | 13 Вт |  | Питание 17FT3003 | СО2 НД ОТ АММИАКА-2 НА КАРБАМИД | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 139500 | kg/h | [26 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F-3008 | 17FT3008 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted |  | DCS_AI_01 | Field |  | 17-С-AD-I-1-FL90 | 15 Pair | Pr.09 | 17-MC-DCS-009 | TS-H-05 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A | O1011005_U8 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | The flow rate of the water-glycol solution directly in the pipeline from Ammonia-2 to Urea | ВОДНО-ГЛИКОЛЕВЫЙ Р-Р ОТ АММИАКА-2 НА КАРБАМИД | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 200 | t/h | [5 empty] | TS-H-05:17/ O1011005_U8:3 | TS-H-05:18/ O1011005_U8:4 |  |  | O1011005:8A/ O1011005_U8:5 | O1011005:8C/ O1011005_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-F-3009 | 17FT3009 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Vortex Flow Transmitter |  | DCS_AI_01 | Field |  | 17-С-AD-I-1-FL90 | 15 Pair | Pr.10 | 17-MC-DCS-009 | TS-H-05 | 19 | 20 |  | 30 | AVK 2,5 A, AVK 2,5 A | O1011005_U9 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | The flow rate of the water-glycol solution of the reverse in the pipeline from Urea to Ammonia-2 | ВОДНО-ГЛИКОЛЕВЫЙ Р-Р ОТ КАРБАМИДА НА АММИАК-2 | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 200 | t/h | [5 empty] | TS-H-05:19/ O1011005_U9:3 | TS-H-05:20/ O1011005_U9:4 |  |  | O1011005:9A/ O1011005_U9:5 | O1011005:9C/ O1011005_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 | 17FSL11301 | 17FSL11301 |  | DI-NIS (VFC) DCS | 30.05.2024 добавлен по TQ_ALL_051 | Сигнал |  |  | DCS_DI_01 |  |  | 17-C-DD-N-001FL11-AH001 | 06 Pair | Pr.04 | 17-MC-DCS-007 | TS-F-18 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-AH-001 CONTINUOUS EMISSION MONITORING SYSTEM | 17-AH-001 СИСТЕМА НЕПРЕРЫВНОГО МОНИТОРИНГА ВЫБРОСОВ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-18:7/ O1011114:16A | TS-F-18:8/ O1011114:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -022LP | 17XSH022LP |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Electric Heater running status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.12 | 17-MC-DCS-005 | TS-G-01 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NAOH storage tank heater 17-L-022-H002 | H002 ПОДОГРЕВАТЕЛЬ NAOH | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:23/ O1011111:12A | TS-G-01:24/ O1011111:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -022LP | 17XSAH022LP |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Electric Heater available status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.13 | 17-MC-DCS-005 | TS-G-01 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NAOH storage tank heater 17-L-022-H002 | L022H002 ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:25/ O1011111:13A | TS-G-01:26/ O1011111:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -022LP | 17XSRH022LP |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Electric Heater remote selection | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.14 | 17-MC-DCS-005 | TS-G-01 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NAOH storage tank heater 17-L-022-H002 | L022H002 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:27/ O1011112:1A | TS-G-01:28/ O1011112:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -022LP | 17XYSPH022LP |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Electric Heater Stop command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.05 | 17-MC-DCS-005 | TS-H-03 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NAOH storage tank heater 17-L-022-H002 | L022H002 ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:6/ O1011209:27A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -022LP | 17XYSTH022LP |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Electric Heater Start command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.07 | 17-MC-DCS-005 | TS-H-03 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NAOH storage tank heater 17-L-022-H002 | L022H002 ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:8/ O1011209:28A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -070851 | 17HY070851 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL07-L073 | 12 Pair | Pr.02 | 17-MC-DCS-006 | TS-Q-02 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011012R_U1 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 1 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071A 92.5% H2SO4 Injection Pump | НАСОС ВПРЫСКА 92,5% H2SO4 | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:3/ O1011012R_U1:3 | TS-Q-02:4/ O1011012R_U1:4 |  |  | O1011012R:1A/ O1011012R_U1:5 | O1011012R:1C/ O1011012R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -070852 | 17HY070852 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL07-L073 | 12 Pair | Pr.03 | 17-MC-DCS-006 | TS-Q-02 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011012R_U2 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 2 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071B 92.5% H2SO4 Injection Pump | НАСОС ВПРЫСКА 92,5% H2SO4 | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:5/ O1011012R_U2:3 | TS-Q-02:6/ O1011012R_U2:4 |  |  | O1011012R:2A/ O1011012R_U2:5 | O1011012R:2C/ O1011012R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -070859 | 17HY070859 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300005 | DCS_AO_02 | Field |  | 17-C-AD-N-004FL07-L073 | 06 Pair | Pr.02 | 17-MC-DCS-008 | TS-O-08 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011014R_U13 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 13 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075A Chlorine Enhancer Injection Pump | НАСОС ВПРЫСКА УСИЛ ХЛОРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:3/ O1011014R_U13:3 | TS-O-08:4/ O1011014R_U13:4 |  |  | O1011014R:13A/ O1011014R_U13:5 | O1011014R:13C/ O1011014R_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -070860 | 17HY070860 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300005 | DCS_AO_02 | Field |  | 17-C-AD-N-004FL07-L073 | 06 Pair | Pr.03 | 17-MC-DCS-008 | TS-O-08 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011014R_U14 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 14 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075B Chlorine Enhancer Injection Pump | НАСОС ВПРЫСКА УСИЛ ХЛОРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:5/ O1011014R_U14:3 | TS-O-08:6/ O1011014R_U14:4 |  |  | O1011014R:14A/ O1011014R_U14:5 | O1011014R:14C/ O1011014R_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -070861 | 17HY070861 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300006 | DCS_AO_02 | Field |  | 17-C-AD-N-005FL07-L073 | 06 Pair | Pr.02 | 17-MC-DCS-006 | TS-R-02 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011012R_U11 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 11 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076A 12-14% Sodium Hypochlorite Inj. | 12-14% ГИПОХЛОР НАТРИЯ ВПРЫСК. | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:3/ O1011012R_U11:3 | TS-R-02:4/ O1011012R_U11:4 |  |  | O1011012R:11A/ O1011012R_U11:5 | O1011012R:11C/ O1011012R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -070862 | 17HY070862 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300006 | DCS_AO_02 | Field |  | 17-C-AD-N-005FL07-L073 | 06 Pair | Pr.03 | 17-MC-DCS-006 | TS-R-02 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011012R_U12 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 12 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076B 12-14% Sodium Hypochlorite Inj. | 12-14% ГИПОХЛОР НАТРИЯ ВПРЫСК. | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:5/ O1011012R_U12:3 | TS-R-02:6/ O1011012R_U12:4 |  |  | O1011012R:12A/ O1011012R_U12:5 | O1011012R:12C/ O1011012R_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -A | 17XSH071A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater ON status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.01 | 17-MC-DCS-005 | TS-F-02 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Gearbox Heater | K071A ПОДОГРЕВАТЕЛЬ МАСЛА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:1/ O1010209:1A | TS-F-02:2/ O1010209:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -A | 17XSAH071A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.02 | 17-MC-DCS-005 | TS-F-02 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Gearbox Heater | 17-HE-07201 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:3/ O1010209:2A | TS-F-02:4/ O1010209:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -A | 17XSRH071A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.03 | 17-MC-DCS-005 | TS-F-02 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Gearbox Heater | 17-HE-07201 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:5/ O1010209:3A | TS-F-02:6/ O1010209:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -A | 17XYSPH071A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.01 | 17-MC-DCS-003 | TS-G-01 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Gearbox Heater | 17-HE-07201 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:2/ O1010212:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -A | 17XYSTH071A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.03 | 17-MC-DCS-003 | TS-G-01 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Gearbox Heater | 17-HE-07201 ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:4/ O1010212:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -B | 17XSH071B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater ON status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.04 | 17-MC-DCS-005 | TS-F-02 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Gearbox Heater | K071B ПОДОГРЕВАТЕЛЬ МАСЛА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:7/ O1010209:4A | TS-F-02:8/ O1010209:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -B | 17XSAH071B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.05 | 17-MC-DCS-005 | TS-F-02 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Gearbox Heater | 17-HE-07202 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:9/ O1010209:5A | TS-F-02:10/ O1010209:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -B | 17XSRH071B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.06 | 17-MC-DCS-005 | TS-F-02 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Gearbox Heater | 17-HE-07202 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:11/ O1010209:6A | TS-F-02:12/ O1010209:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -B | 17XYSPH071B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.05 | 17-MC-DCS-003 | TS-G-01 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Gearbox Heater | 17-HE-07202 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:6/ O1010212:3A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -B | 17XYSTH071B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.07 | 17-MC-DCS-003 | TS-G-01 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Gearbox Heater | 17-HE-07202 ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:8/ O1010212:4A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -C | 17XSH071C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater ON status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.01 | 17-MC-DCS-003 | TS-F-02 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Gearbox Heater | K071C ПОДОГРЕВАТЕЛЬ МАСЛА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:1/ O1010206:1A | TS-F-02:2/ O1010206:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -C | 17XSAH071C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.02 | 17-MC-DCS-003 | TS-F-02 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Gearbox Heater | 17-HE-07203 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:3/ O1010206:2A | TS-F-02:4/ O1010206:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -C | 17XSRH071C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.03 | 17-MC-DCS-003 | TS-F-02 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Gearbox Heater | 17-HE-07203 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:5/ O1010206:3A | TS-F-02:6/ O1010206:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -C | 17XYSPH071C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.09 | 17-MC-DCS-003 | TS-G-01 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Gearbox Heater | 17-HE-07203 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:10/ O1010212:5A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -C | 17XYSTH071C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.11 | 17-MC-DCS-003 | TS-G-01 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Gearbox Heater | 17-HE-07203 ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:12/ O1010212:6A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -D | 17XSH071D |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater ON status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.04 | 17-MC-DCS-003 | TS-F-02 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Gearbox Heater | K071D ПОДОГРЕВАТЕЛЬ МАСЛА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:7/ O1010206:4A | TS-F-02:8/ O1010206:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -D | 17XSAH071D |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.05 | 17-MC-DCS-003 | TS-F-02 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Gearbox Heater | 17-HE-07204 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:9/ O1010206:5A | TS-F-02:10/ O1010206:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -D | 17XSRH071D |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.06 | 17-MC-DCS-003 | TS-F-02 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Gearbox Heater | 17-HE-07204 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:11/ O1010206:6A | TS-F-02:12/ O1010206:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -D | 17XYSPH071D |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.13 | 17-MC-DCS-003 | TS-G-01 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Gearbox Heater | 17-HE-07204 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:14/ O1010212:7A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -D | 17XYSTH071D |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.15 | 17-MC-DCS-003 | TS-G-01 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Gearbox Heater | 17-HE-07204 ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:16/ O1010212:8A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -E | 17XSH071E |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater ON status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.07 | 17-MC-DCS-003 | TS-F-02 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Gearbox Heater | K071E ПОДОГРЕВАТЕЛЬ МАСЛА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:13/ O1010206:7A | TS-F-02:14/ O1010206:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -E | 17XSAH071E |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.07 | 17-MC-DCS-005 | TS-F-02 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Gearbox Heater | 17-HE-07205 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:13/ O1010209:7A | TS-F-02:14/ O1010209:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -E | 17XSRH071E |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.08 | 17-MC-DCS-005 | TS-F-02 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Gearbox Heater | 17-HE-07205 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:15/ O1010209:8A | TS-F-02:16/ O1010209:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -E | 17XYSPH071E |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.17 | 17-MC-DCS-003 | TS-G-01 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Gearbox Heater | 17-HE-07205 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:18/ O1010212:9A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -E | 17XYSTH071E |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.19 | 17-MC-DCS-003 | TS-G-01 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Gearbox Heater | 17-HE-07205 ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:20/ O1010212:10A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -F | 17XSH071F |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater ON status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.09 | 17-MC-DCS-005 | TS-F-02 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Gearbox Heater | K071F ПОДОГРЕВАТЕЛЬ МАСЛА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:17/ O1010209:9A | TS-F-02:18/ O1010209:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -F | 17XSAH071F |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.10 | 17-MC-DCS-005 | TS-F-02 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Gearbox Heater | 17-HE-07206 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:19/ O1010209:10A | TS-F-02:20/ O1010209:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -F | 17XSRH071F |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.11 | 17-MC-DCS-005 | TS-F-02 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Gearbox Heater | 17-HE-07206 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:21/ O1010209:11A | TS-F-02:22/ O1010209:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -F | 17XYSPH071F |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.21 | 17-MC-DCS-003 | TS-G-01 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Gearbox Heater | 17-HE-07206 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:22/ O1010212:11A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -F | 17XYSTH071F |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-005BL02 | 30 Core | C.23 | 17-MC-DCS-003 | TS-G-01 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Gearbox Heater | 17-HE-07206 ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-01:24/ O1010212:12A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -G | 17XSH071G |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater ON status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.12 | 17-MC-DCS-005 | TS-F-02 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Gearbox Heater | K071G ПОДОГРЕВАТЕЛЬ МАСЛА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:23/ O1010209:12A | TS-F-02:24/ O1010209:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -G | 17XSAH071G |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.13 | 17-MC-DCS-005 | TS-F-02 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Gearbox Heater | 17-HE-07207 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:25/ O1010209:13A | TS-F-02:26/ O1010209:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -G | 17XSRH071G |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.14 | 17-MC-DCS-005 | TS-F-02 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Gearbox Heater | 17-HE-07207 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:27/ O1010209:14A | TS-F-02:28/ O1010209:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -G | 17XYSPH071G |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.01 | 17-MC-DCS-003 | TS-G-08 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Gearbox Heater | 17-HE-07207 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:2/ O1010214:19A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -G | 17XYSTH071G |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.03 | 17-MC-DCS-003 | TS-G-08 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Gearbox Heater | 17-HE-07207 ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:4/ O1010214:20A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -H | 17XSRH071H |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.17 | 17-MC-DCS-005 | TS-F-02 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Gearbox Heater | 17-HE-07208 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:33/ O1010115:10A | TS-F-02:34/ O1010115:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -H | 17XSH071H |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater ON status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.15 | 17-MC-DCS-005 | TS-F-02 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Gearbox Heater | K071H ПОДОГРЕВАТЕЛЬ МАСЛА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:29/ O1010209:15A | TS-F-02:30/ O1010209:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -H | 17XSAH071H |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.16 | 17-MC-DCS-005 | TS-F-02 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Gearbox Heater | 17-HE-07208 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:31/ O1010209:16A | TS-F-02:32/ O1010209:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -H | 17XYSPH071H |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.05 | 17-MC-DCS-003 | TS-G-08 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Gearbox Heater | 17-HE-07208 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:6/ O1010214:21A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -071 -H | 17XYSTH071H |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.07 | 17-MC-DCS-003 | TS-G-08 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Gearbox Heater | 17-HE-07208 ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:8/ O1010214:22A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -090213 | 17XS090213X |  | DI-NIS (VFC) DCS |  | Сигнал | Exchange Signal | 4124-GY-VD-BD17517L091090 | DCS_DI_01 | RR-AM |  | 17-I-DD-N-001-BL02-L091 | 06 Pair | Pr.06 | 17-MC-DCS-007 | TS-F-17 | 11 | 12 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAULT STATUS OF PLCs | СТАТУС ОШИБКИ КОНТРОЛЛЕРА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-17:11/ O1011113:23A | TS-F-17:12/ O1011113:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -090301 | 17HS090301 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003A-L091 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-03 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Dryer Start for TRAIN A | ПУСК ОСУШКИ ПОТОКА А | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:1/ O1011113:29A | TS-F-03:2/ O1011113:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -090302 | 17HS090302 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003A-L091 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-03 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Dryer STOP TRAIN A | СТОП ОСУШКИ ПОТОКА А | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:3/ O1011113:30A | TS-F-03:4/ O1011113:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -090303 | 17HS090303 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003A-L091 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-F-03 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Dryer LAMP TEST TRAIN A | ПРОВЕРКА ЛАМП ОСУШКИ ПОТОКА А | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP TEST | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:5/ O1011113:31A | TS-F-03:6/ O1011113:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -090304 | 17HS090304 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003A-L091 | 06 Pair | Pr.04 | 17-MC-DCS-007 | TS-F-03 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Dryer LOCAL/REMOTE TRAIN A | ОСУШКА ПОТОКА А МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:7/ O1011113:32A | TS-F-03:8/ O1011113:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -090351 | 17HS090351 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003B-L091 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-04 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Dryer Start for TRAIN B | ПУСК ОСУШКИ ПОТОКА В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:1/ O1011114:8A | TS-F-04:2/ O1011114:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -090352 | 17HS090352 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003B-L091 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-04 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Dryer STOP TRAIN B | СТОП ОСУШКИ ПОТОКА В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:3/ O1011114:9A | TS-F-04:4/ O1011114:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -090353 | 17HS090353 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003B-L091 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-F-04 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Dryer LAMP TEST TRAIN B | ПРОВЕРКА ЛАМП ОСУШКИ ПОТОКА В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP TEST | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:5/ O1011114:10A | TS-F-04:6/ O1011114:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -090354 | 17HS090354 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003B-L091 | 06 Pair | Pr.04 | 17-MC-DCS-007 | TS-F-04 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Dryer LOCAL/REMOTE TRAIN B | ОСУШКА ПОТОКА В МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:7/ O1011114:11A | TS-F-04:8/ O1011114:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100245 | 17HS100245AY |  | DO-NIS (VFC NO) DCS |  | Сигнал | Exchange Signal | 4124-FY-VD-BD17517L10100002 | DCS_DO_02 | RR-AM |  | 17-I-DD-N-002-BL02-L101 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-H-04 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Nitrogen Package OSS Train A activation command | ПОДАЧА АЗОТА ТРЕНИРОВКА А | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC-S | POS ACTIVE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-04:1/ O1011211:5A | TS-H-04:2/ O1011211:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100245 | 17HS100245BY |  | DO-NIS (VFC NO) DCS |  | Сигнал | Exchange Signal | 4124-FY-VD-BD17517L10100002 | DCS_DO_02 | RR-AM |  | 17-I-DD-N-002-BL02-L101 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-H-04 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Nitrogen Package OSS Train B activation command | ПОДАЧА АЗОТА ТРЕНИРОВКА В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC-S | POS ACTIVE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-04:3/ O1011211:6A | TS-H-04:4/ O1011211:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100701 | 17HS100701 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_01 | LP |  | 17-C-DD-001-LP001-K101 | 12 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-01 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR SEQUENCE START BUTTON | КНОПКА ПУСКА КОМПРЕССОРА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-01:1/ O1011113:1A | TS-F-01:2/ O1011113:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100702 | 17HS100702 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_01 | LP |  | 17-C-DD-001-LP001-K101 | 12 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-01 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR SEQUENCE STOP BUTTON | КНОПКА ПУСКА КОМПРЕССОРА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-01:3/ O1011113:2A | TS-F-01:4/ O1011113:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100703 | 17HS100703 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_01 | LP |  | 17-C-DD-001-LP001-K101 | 12 Pair | Pr.03 | 17-MC-DCS-007 | TS-F-01 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LAMP TEST BUTTON | КНОПКА ПРОВЕРКИ ЛАМП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP TEST | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-01:5/ O1011113:3A | TS-F-01:6/ O1011113:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100704 | 17HS100704 |  | DI-NIS (VFC) DCS |  | Сигнал | Reset Switch | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_01 | LP |  | 17-C-DD-001-LP001-K101 | 12 Pair | Pr.04 | 17-MC-DCS-007 | TS-F-01 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | RESET BUTTON | КНОПКА СБРОСА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RESET | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-01:7/ O1011113:4A | TS-F-01:8/ O1011113:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100705 | 17HS100705A |  | DI-NIS (VFC) DCS |  | Сигнал | Selector Switch | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_01 | LP |  | 17-C-DD-001-LP001-K101 | 12 Pair | Pr.05 | 17-MC-DCS-007 | TS-F-01 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 0-50 % CAPACITY SELECTOR | ВЫБОР МОЩНОСТИ 0-50% | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | 50 % SELECTED | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-01:9/ O1011113:5A | TS-F-01:10/ O1011113:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100705 | 17HS100705B |  | DI-NIS (VFC) DCS |  | Сигнал | Selector Switch | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_01 | LP |  | 17-C-DD-001-LP001-K101 | 12 Pair | Pr.09 | 17-MC-DCS-007 | TS-F-01 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 50-100 % CAPACITY SELECTOR | ВЫБОР МОЩНОСТИ 0-100% | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | 100 % SELECTED | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-01:17/ O1011114:1A | TS-F-01:18/ O1011114:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100706 | 17HS100706 |  | DI-NIS (VFC) DCS |  | Сигнал | Selector Switch | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_01 | LP |  | 17-C-DD-001-LP001-K101 | 12 Pair | Pr.06 | 17-MC-DCS-007 | TS-F-01 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LOCAL / REMOTE SELECTOR | ВЫБОР МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-01:11/ O1011113:6A | TS-F-01:12/ O1011113:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100722 | 17XY100722 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_01 | Field |  | 17-C-DD-002-LP001-K101 | 30 Core | C.11 | 17-MC-DCS-007 | TS-G-01 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 6 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | CAPACITY CONTROL 0-50% | УПРАВЛЕНИЕ МОЩНОСТЬЮ 0-50% | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-G-01:11/ O1011210:6A | TS-G-01:12/ O1011210:6C | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -100723 | 17XY100723 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_01 | Field |  | 17-C-DD-002-LP001-K101 | 30 Core | C.13 | 17-MC-DCS-007 | TS-G-01 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 7 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | CAPACITY CONTROL 100% | УПРАВЛЕНИЕ МОЩНОСТЬЮ 100% | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-G-01:13/ O1011210:7A | TS-G-01:14/ O1011210:7C | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -101K | 17XSH101K |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.01 | 17-MC-DCS-003 | TS-F-05 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR LUBE OIL HEATER 17-K-101-H-101 | НАГРЕВАТЕЛЬ МАСЛА КОМПРЕССОРА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-05:1/ O1010207:25A | TS-F-05:2/ O1010207:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -101K | 17XSAH101K |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.02 | 17-MC-DCS-003 | TS-F-05 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR LUBE OIL HEATER 17-K-101-H-101 | 17K101H101 ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-05:3/ O1010207:26A | TS-F-05:4/ O1010207:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -101K | 17XSRH101K |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.03 | 17-MC-DCS-003 | TS-F-05 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR LUBE OIL HEATER 17-K-101-H-101 | 17K101H101 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-05:5/ O1010207:27A | TS-F-05:6/ O1010207:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -101K | 17XYSPH101K |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.05 | 17-MC-DCS-003 | TS-G-05 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR LUBE OIL HEATER 17-K-101-H-101 | 17K101H101 СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:6/ O1010213:21A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -101K | 17XYSTH101K |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.07 | 17-MC-DCS-003 | TS-G-05 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR LUBE OIL HEATER 17-K-101-H-101 | 17K101H101 ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:8/ O1010213:22A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111L -001 | 17XSH111L001 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Running Status | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.07 | 17-MC-DCS-005 | TS-G-04 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LO Heater 17-STP-111A-H-001 | ПАРОВАЯ ТУРБИНА НАСОСА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:13/ O1010115:32A | TS-G-04:14/ O1010115:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111L -001 | 17XYSPH111L001 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Stop command | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.09 | 17-MC-DCS-003 | TS-G-07 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LO Heater 17-STP-111A-H-001 | 17-STP-111A-H-001 СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:10/ O1010214:9A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111L -001 | 17XYSTH111L001 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Start command | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.11 | 17-MC-DCS-003 | TS-G-07 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LO Heater 17-STP-111A-H-001 | 17-STP-111A-H-001 ПУСК | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:12/ O1010214:10A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111L -001 | 17XSAH111L001 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater available status | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.08 | 17-MC-DCS-005 | TS-G-04 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LO Heater 17-STP-111A-H-001 | 17-STP-111A-H-001 ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:15/ O1010300:1A | TS-G-04:16/ O1010300:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111L -001 | 17XSRH111L001 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Heater Local/Remote status | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.09 | 17-MC-DCS-005 | TS-G-04 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LO Heater 17-STP-111A-H-001 | 17-STP-111A-H-001 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:17/ O1010300:2A | TS-G-04:18/ O1010300:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111LP | 17XSH111LP |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FB-VD-BD00317L11111309 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.01 | 17-MC-DCS-005 | TS-G-04 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-111-H-111 Electric heater | ЭЛЕКТРОНАГРЕВАТЕЛЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:1/ O1010115:26A | TS-G-04:2/ O1010115:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111LP | 17XSAH111LP |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Electric Heater available status | 4124-FB-VD-BD00317L11111309 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.02 | 17-MC-DCS-005 | TS-G-04 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-111-H-111 Electric heater | 17-L-111-H-111 ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:3/ O1010115:27A | TS-G-04:4/ O1010115:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111LP | 17XSRH111LP |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FB-VD-BD00317L11111309 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.03 | 17-MC-DCS-005 | TS-G-04 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-111-H-111 Electric heater | 17-L-111-H-111 МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:5/ O1010115:28A | TS-G-04:6/ O1010115:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111LP | 17XYSPH111LP |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FB-VD-BD00317L11111309 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.01 | 17-MC-DCS-003 | TS-G-07 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-111-H-111 Electric heater | 17-L-111-H-111 СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:2/ O1010214:5A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -111LP | 17XYSTH111LP |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FB-VD-BD00317L11111309 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.03 | 17-MC-DCS-003 | TS-G-07 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-111-H-111 Electric heater | 17-L-111-H-111 ПУСК | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:4/ O1010214:6A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -11250 -A | 17HS11250A |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GG-VD-BD17117P111037_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP001-P111A | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-15 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Start | ПУСК ТУРБИНЫ СИГНАЛИЗАЦИЯ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-15:1/ O1011114:2A | TS-F-15:2/ O1011114:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -11250 -B | 17HS11250B |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GG-VD-BD17117P111037_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP001-P111A | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-15 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Stop | СТОП ТУРБИНЫ СИГНАЛИЗАЦИЯ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-15:3/ O1011114:3A | TS-F-15:4/ O1011114:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -11250 -C | 17HS11250C |  | DI-NIS (VFC) DCS |  | Сигнал | Local Remote Switch | 4124-GG-VD-BD17117P111037_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP001-P111A | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-F-15 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Local / Remote | ТУРБИНА МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-15:5/ O1011114:4A | TS-F-15:6/ O1011114:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -11250 -D | 17HS11250D |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GG-VD-BD17117P111037_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP001-P111A | 06 Pair | Pr.04 | 17-MC-DCS-007 | TS-F-15 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Speed Raise | ТУРБИНА ПОВЫШЕННАЯ СКОРОСТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RAISE | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-15:7/ O1011114:5A | TS-F-15:8/ O1011114:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -11250 -E | 17HS11250E |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GG-VD-BD17117P111037_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP001-P111A | 06 Pair | Pr.05 | 17-MC-DCS-007 | TS-F-15 | 9 | 10 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Speed Lower | ТУРБИНА МАЛАЯ СКОРОСТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LOWER | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-15:9/ O1011114:6A | TS-F-15:10/ O1011114:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -11250 -F | 17HS11250F |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-GG-VD-BD17117P111037_SH.2 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP001-P111A | 06 Pair | Pr.06 | 17-MC-DCS-007 | TS-F-15 | 11 | 12 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine LP Lamp Test | Испытание лампы низкого давления турбины | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | TEST | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-15:11/ O1011114:7A | TS-F-15:12/ O1011114:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.12 |  | Резерв |  | DO-NIS (VFC NO) DCS | 08.04.25 сигнал 17HS11281Y исключен по TQ-132 | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 1 | DO716-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-G-04 клеммы 1,2 до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.12 |  | Резерв |  | DO-NIS (VFC NO) DCS | 08.04.25 сигнал 17HS11281R исключен по TQ-132 | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 2 | DO716-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-G-04 клеммы 3, 4 до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -113930 | 17HS113930A |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-FB-VD-BD00317L11111310 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP002-L111 | 12 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-02 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE START | ПУСК ПАРОВОЙ ТУРБИНЫ СИГНАЛИЗ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:1/ O1011113:24A | TS-F-02:2/ O1011113:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -113931 | 17HS113931A |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-FB-VD-BD00317L11111310 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP002-L111 | 12 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-02 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE STOP | СТОП ПАРОВОЙ ТУРБИНЫ СИГНАЛИЗ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:3/ O1011113:25A | TS-F-02:4/ O1011113:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -113932 | 17HS113932 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-FB-VD-BD00317L11111310 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP002-L111 | 12 Pair | Pr.03 | 17-MC-DCS-007 | TS-F-02 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE HAND/OFF/AUTO | ПАРОВАЯ ТУРБИНА РУЧН/ВЫКЛ/АВТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AUTO | MANUAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:5/ O1011113:26A | TS-F-02:6/ O1011113:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -113933 | 17HS113933 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-FB-VD-BD00317L11111310 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP002-L111 | 12 Pair | Pr.04 | 17-MC-DCS-007 | TS-F-02 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE RAISE SPEED | ПАРОВАЯ ТУРБИНА СКОРОСТЬ МАХ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RAISE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:7/ O1011113:27A | TS-F-02:8/ O1011113:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -113934 | 17HS113934 |  | DI-NIS (VFC) DCS |  | Сигнал | Hand Switch | 4124-FB-VD-BD00317L11111310 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP002-L111 | 12 Pair | Pr.05 | 17-MC-DCS-007 | TS-F-02 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE LOWER SPEED | ПАРОВАЯ ТУРБИНА НИЗКАЯ СКОРОСТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LOWER | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:9/ O1011113:28A | TS-F-02:10/ O1011113:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -113938 | 17HS113938Y |  | DO-NIS (VFC NO) DCS |  | Сигнал | Hand Switch | 4124-FB-VD-BD00317L11111310 | DCS_DO_02 | RR-AM |  | 17-I-DD-N-022BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-04 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-111-STK-101-A Start Command TO OST | КОМАНДА ПУСК 17-L-111-STK-101-A | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | OST | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:5/ O1011211:3A | TS-G-04:6/ O1011211:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -113938 | 17HS113938R |  | DO-NIS (VFC NO) DCS |  | Сигнал | Reset Switch | 4124-FB-VD-BD00317L11111310 | DCS_DO_02 | RR-AM |  | 17-I-DD-N-022BL02 | 06 Pair | Pr.04 | 17-MC-DCS-007 | TS-G-04 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-111-STK-101-A RESET TO OST | КОМАНДА СБРОС 17-L-111-STK-101-A | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | OST | RESET | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:7/ O1011211:4A | TS-G-04:8/ O1011211:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -11501 | 17HY11501 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17117L11200001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.07 | 17-MC-DCS-006 | TS-R-01 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011012R_U5 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 5 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001A Sodium Phosphate Injection Pump | НАСОС ВПРЫСКА ФОСФАТА НАТРИЯ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:13/ O1011012R_U5:3 | TS-R-01:14/ O1011012R_U5:4 |  |  | O1011012R:5A/ O1011012R_U5:5 | O1011012R:5C/ O1011012R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -11502 | 17HY11502 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17117L11200001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.08 | 17-MC-DCS-006 | TS-R-01 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011012R_U6 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 6 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001B Sodium Phosphate Injection Pump | НАСОС ВПРЫСКА ФОСФАТА НАТРИЯ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:15/ O1011012R_U6:3 | TS-R-01:16/ O1011012R_U6:4 |  |  | O1011012R:6A/ O1011012R_U6:5 | O1011012R:6C/ O1011012R_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -115100 | 17HY115100 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17117L11300001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.09 | 17-MC-DCS-006 | TS-R-01 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011012R_U7 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 7 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001A Oxygen Scavenger Injection Pump | НАСОС ВПРЫСКА ПОГЛОТ О2 | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:17/ O1011012R_U7:3 | TS-R-01:18/ O1011012R_U7:4 |  |  | O1011012R:7A/ O1011012R_U7:5 | O1011012R:7C/ O1011012R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -115101 | 17HY115101 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17117L11300001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.10 | 17-MC-DCS-006 | TS-R-01 | 19 | 20 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011012R_U8 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 8 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001B Oxygen Scavenger Injection Pump | НАСОС ВПРЫСКА ПОГЛОТ О2 | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:19/ O1011012R_U8:3 | TS-R-01:20/ O1011012R_U8:4 |  |  | O1011012R:8A/ O1011012R_U8:5 | O1011012R:8C/ O1011012R_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -115300 | 17HY115300 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17117L11400001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.11 | 17-MC-DCS-006 | TS-R-01 | 21 | 22 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011012R_U9 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 9 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001A Amine Injection Pump | 17114P001A НАСОС ВПРЫСКА АМИНА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:21/ O1011012R_U9:3 | TS-R-01:22/ O1011012R_U9:4 |  |  | O1011012R:9A/ O1011012R_U9:5 | O1011012R:9C/ O1011012R_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-H -115301 | 17HY115301 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17117L11400001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.12 | 17-MC-DCS-006 | TS-R-01 | 23 | 24 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011012R_U10 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 10 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001B Amine Injection Pump | 17114P001В НАСОС ВПРЫСКА АМИНА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:23/ O1011012R_U10:3 | TS-R-01:24/ O1011012R_U10:4 |  |  | O1011012R:10A/ O1011012R_U10:5 | O1011012R:10C/ O1011012R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-H-070853 | 17-HY-070853 |  | AO-R-NIS (4-20 mA) DCS | 24.09.24 сигнал добавлен по TQ_ALL_81 | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300002 | DCS_AO_02 |  |  | 17-C-AD-N-002FL07-L073 | 06 Pair | Pr. 02 | 17-MC-DCS-008 | TS-O-04 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010108R_U15 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 15 | AO713-H11 | 16 |  |  | смонтировать провода от клеммника до терм платы |  | 17-L-073-PM-072A Corrosion Inhibitor Injection Pump | 17-L-073-PM-072A Насос ингибитора коррозии | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [16 empty] | TS-O-04:3/ O1010108R_U15:3 | TS-O-04:4/ O1010108R_U15:4 |  |  | O1010108R:15A/ O1010108R_U15:5 | O1010108R:15C/ O1010108R_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-H-070854 | 17-HY-070854 |  | AO-R-NIS (4-20 mA) DCS | 24.09.24 сигнал добавлен по TQ_ALL_81 | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300002 | DCS_AO_02 |  |  | 17-C-AD-N-002FL07-L073 | 06 Pair | Pr. 03 | 17-MC-DCS-008 | TS-O-04 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010108R_U16 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 16 | AO713-H11 | 16 |  |  | смонтировать провода от клеммника до терм платы |  | 17-L-073-PM-072B Corrosion Inhibitor Injection Pump | 17-L-073-PM-072B Насос ингибитора коррозии | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [16 empty] | TS-O-04:5/ O1010108R_U16:3 | TS-O-04:6/ O1010108R_U16:4 |  |  | O1010108R:16A/ O1010108R_U16:5 | O1010108R:16C/ O1010108R_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-H-070855 | 17-HY-070855 |  | AO-R-NIS (4-20 mA) DCS | 24.09.24 сигнал добавлен по TQ_ALL_81 | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300003 | DCS_AO_02 |  |  | 17-C-AD-N-003FL07-L073 | 06 Pair | Pr. 02 | 17-MC-DCS-008 | TS-O-07 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011302R_U10 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 10 | AO713-H11 | 16 |  |  | смонтировать провода от клеммниа до барьера | DCS AMMONIA-UTILITIES | 17-L-073-PM-073A Dispersant Injection Pump | 17-L-073-PM-073A Насос диспергатора | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [16 empty] | TS-O-07:3/ O1011302R_U10:3 | TS-O-07:4/ O1011302R_U10:4 |  |  | O1011302R:10A/ O1011302R_U10:5 | O1011302R:10C/ O1011302R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-H-070856 | 17-HY-070856 |  | AO-R-NIS (4-20 mA) DCS | 24.09.24 сигнал добавлен по TQ_ALL_81 | Сигнал | Electric Stroke Actuator | 4124-FY-VD-BD17217L07300003 | DCS_AO_02 |  |  | 17-C-AD-N-003FL07-L073 | 06 Pair | Pr. 03 | 17-MC-DCS-008 | TS-O-07 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011302R_U11 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 11 | AO713-H11 | 16 |  |  | смонтировать провода от клеммниа до барьера | DCS AMMONIA-UTILITIES | 17-L-073-PM-073B Dispersant Injection Pump | 17-L-073-PM-073B Насос диспергатора | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [16 empty] | TS-O-07:5/ O1011302R_U11:3 | TS-O-07:6/ O1011302R_U11:4 |  |  | O1011302R:11A/ O1011302R_U11:5 | O1011302R:11C/ O1011302R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.4 | 17-I-0701 | 17XA00701 |  | DI-NIS (24VDC) DCS | 06.08.2024 добавлен резервированный модуль 01.08.2024 добавлен (передача блокировки из ПАЗ) | Сигнал |  |  | DCS_DI_07 |  |  | 17-I-DD-N-201BL02 | 12 Pair | Pr. 01 | 17-MC-DCS-001 | TS-G-09 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010304R | TUA711-DIR32 | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-I-0701 | Передача блокировки 17-I-0701 от ПАЗ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09 :1/ O1010304R:1A | TS-G-09 :2/ O1010304R:1B | [12 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.4 | 17-I-1002 | 17XA01002 |  | DI-NIS (24VDC) DCS | 06.08.2024 добавлен резервированный модуль 01.08.2024 добавлен (передача блокировки из ПАЗ) | Сигнал |  |  | DCS_DI_07 |  |  | 17-I-DD-N-201BL02 | 12 Pair | Pr. 06 | 17-MC-DCS-001 | TS-G-09 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010304R | TUA711-DIR32 | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-I-1002 | Передача блокировки 17-I-1002 от ПАЗ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09 :11/ O1010304R:6A | TS-G-09 :12/ O1010304R:6B | [12 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.4 | 17-I-1004 | 17XA01004 |  | DI-NIS (24VDC) DCS | 06.08.2024 добавлен резервированный модуль 01.08.2024 добавлен (передача блокировки из ПАЗ) | Сигнал |  |  | DCS_DI_07 |  |  | 17-I-DD-N-201BL02 | 12 Pair | Pr. 07 | 17-MC-DCS-001 | TS-G-09 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010304R | TUA711-DIR32 | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-I-1004 | Передача блокировки 17-I-1004 от ПАЗ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09 :13/ O1010304R:7A | TS-G-09 :14/ O1010304R:7B | [12 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.4 | 17-I-1103 | 17XA01103 |  | DI-NIS (24VDC) DCS | 06.08.2024 добавлен резервированный модуль 01.08.2024 добавлен (передача блокировки из ПАЗ) | Сигнал |  |  | DCS_DI_07 |  |  | 17-I-DD-N-201BL02 | 12 Pair | Pr. 02 | 17-MC-DCS-001 | TS-G-09 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010304R | TUA711-DIR32 | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-I-1103 | Передача блокировки 17-I-0703 от ПАЗ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09 :3/ O1010304R:2A | TS-G-09 :4/ O1010304R:2B | [12 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.4 | 17-I-1104 | 17XA01104 |  | DI-NIS (24VDC) DCS | 06.08.2024 добавлен резервированный модуль 01.08.2024 добавлен (передача блокировки из ПАЗ) | Сигнал |  |  | DCS_DI_07 |  |  | 17-I-DD-N-201BL02 | 12 Pair | Pr. 03 | 17-MC-DCS-001 | TS-G-09 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010304R | TUA711-DIR32 | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-I-1104 | Передача блокировки 17-I-0704 от ПАЗ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09 :5/ O1010304R:3A | TS-G-09 :6/ O1010304R:3B | [12 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.4 | 17-I-1106 | 17XA01106 |  | DI-NIS (24VDC) DCS | 06.08.2024 добавлен резервированный модуль 01.08.2024 добавлен (передача блокировки из ПАЗ) | Сигнал |  |  | DCS_DI_07 |  |  | 17-I-DD-N-201BL02 | 12 Pair | Pr. 04 | 17-MC-DCS-001 | TS-G-09 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010304R | TUA711-DIR32 | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-I-1106 | Передача блокировки 17-I-0706 от ПАЗ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09 :7/ O1010304R:4A | TS-G-09 :8/ O1010304R:4B | [12 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.4 | 17-I-1107 | 17XA01107 |  | DI-NIS (24VDC) DCS | 06.08.2024 добавлен резервированный модуль 01.08.2024 добавлен (передача блокировки из ПАЗ) | Сигнал |  |  | DCS_DI_07 |  |  | 17-I-DD-N-201BL02 | 12 Pair | Pr. 05 | 17-MC-DCS-001 | TS-G-09 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010304R | TUA711-DIR32 | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-I-1107 | Передача блокировки 17-I-0707 от ПАЗ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09 :9/ O1010304R:5A | TS-G-09 :10/ O1010304R:5B | [12 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -020200 | 17LT020200 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level TX- Diaphragm seal & capillary | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_AI_01 | Field |  | 17-C-AD-N-005FL03-L022 | 06 Pair | Pr.04 | 17-MC-DCS-008 | TS-O-09 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011004_U10 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Daily tank | БАК H2SO4 НА ДЕМ ВОДЕ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 15 | 85 |  | 0 | 100 | % | [5 empty] | TS-O-09:7/ O1011004_U10:3 | TS-O-09:8/ O1011004_U10:4 |  |  | O1011004:10A/ O1011004_U10:5 | O1011004:10C/ O1011004_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -020204 | 17LT020204 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level TX- Diaphragm seal & capillary | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_AI_01 | Field |  | 17-C-AD-N-005FL03-L022 | 06 Pair | Pr.01 | 17-MC-DCS-008 | TS-O-09 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011003_U16 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | NaOH storage tank | БАК NAOH НА ДЕМ ВОДЕ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 10 | 85 |  | 0 | 100 | % | [5 empty] | TS-O-09:1/ O1011003_U16:3 | TS-O-09:2/ O1011003_U16:4 |  |  | O1011003:16A/ O1011003_U16:5 | O1011003:16C/ O1011003_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -020206 | 17LT020206 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_AI_01 | Field |  | 17-C-AD-N-006FL03-L022 | 24 Pair | Pr.07 | 17-MC-DCS-008 | TS-P-03 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011004_U15 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022A | БАСЕЙН НЕЙТРАЛИЗАЦИИ BS-022A | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 18 | 85 |  | 0 | 3750 | mm | [5 empty] | TS-P-03:13/ O1011004_U15:3 | TS-P-03:14/ O1011004_U15:4 |  |  | O1011004:15A/ O1011004_U15:5 | O1011004:15C/ O1011004_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -020208 | 17LT020208 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_AI_01 | Field |  | 17-C-AD-N-006FL03-L022 | 24 Pair | Pr.08 | 17-MC-DCS-008 | TS-P-03 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011004_U16 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022B | БАСЕЙН НЕЙТРАЛИЗАЦИИ BS-022B | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 18 | 85 |  | 0 | 3750 | mm | [5 empty] | TS-P-03:15/ O1011004_U16:3 | TS-P-03:16/ O1011004_U16:4 |  |  | O1011004:16A/ O1011004_U16:5 | O1011004:16C/ O1011004_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -02084 | 17LT02084 | 17-ID-0201 | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21702020 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.05 | 17-MC-DCS-006 | TS-Q-05 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U13 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-021 Vessel Level | БАК НЕКОНД КОНДЕНСАТА T-021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 4.3 | 92.3 |  | 0 | 100 | % | [5 empty] | TS-Q-05:9/ O1010005_U13:3 | TS-Q-05:10/ O1010005_U13:4 |  |  | O1010005:13A/ O1010005_U13:5 | O1010005:13C/ O1010005_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -02084 | 17LI02084AY |  | AO-NIS (4-20 mA) DCS |  | Сигнал | Loop Powered Indicator | 4124-XZ-DM-21702020 | DCS_AO_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.18 | 17-MC-DCS-006 | TS-Q-04 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010114_U1 | HD5546 | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 1 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-021 Vessel Level | УРОВЕНЬ В БАКЕ 17-T-021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:35/ O1010114_U1:3 | TS-Q-04:36/ O1010114_U1:4 |  |  | O1010114:1A/ O1010114_U1:5 | O1010114:1C/ O1010114_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -03001 | 17LT03001 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21703001 | DCS_AI_02 | Field |  | 17-LT-03001 | 01 Pair | Pr.01 | 17-MC-DCS-008 | TS-P-05 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A | O1010100R_U5 | HD5542 | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-032 Vessel Level | ЕМКОСТЬ ДЕМ ВОДЫ T-032 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 8 | 94 |  | 0 | 100 | % | [5 empty] | TS-P-05:1/ O1010100R_U5:3 | TS-P-05:2/ O1010100R_U5:4 |  |  | O1010100R:5A/ O1010100R_U5:5 | O1010100R:5C/ O1010100R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -03001 | 17LY03001 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21703001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.06 | 17-MC-DCS-006 | TS-O-02 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U12 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 12 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | DM Water to 17-T-032 | ДЕМ ВОДА В 17-T-032 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-O-02:11/ O1010104R_U12:3 | TS-O-02:12/ O1010104R_U12:4 |  |  | O1010104R:12A/ O1010104R_U12:5 | O1010104R:12C/ O1010104R_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -03003 | 17LZI03003AY |  | AO-NIS (4-20 mA) DCS |  | Сигнал | Loop Powered Indicator | 4124-XZ-DM-21703001 | DCS_AO_01 | Field |  | 17-LZI-03003A | 01 Pair | Pr.01 | 17-MC-DCS-006 | TS-R-04 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A | O1010114_U4 | HD5546 | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 4 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-032 Vessel Level | УРОВЕНЬ ДЕМ ВОДЫ В 17-T-032 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-R-04:1/ O1010114_U4:3 | TS-R-04:2/ O1010114_U4:4 |  |  | O1010114:4A/ O1010114_U4:5 | O1010114:4C/ O1010114_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -03012 | 17LT03012 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21703006 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.12 | 17-MC-DCS-006 | TS-Q-04 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U4 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-020 Level | СБОРНИК ПАРОВОГО КОНДЕНСАТА 17-V-020 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 13.7 | 71.8 |  | 0 | 100 | % | [5 empty] | TS-Q-04:23/ O1010005_U4:3 | TS-Q-04:24/ O1010005_U4:4 |  |  | O1010005:4A/ O1010005_U4:5 | O1010005:4C/ O1010005_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -03021 | 17LT03021 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.06 | 17-MC-DCS-006 | TS-Q-05 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U14 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-030 Level | СБОРНИК ТЕХНОЛОГИЧЕСКОГО КОНДЕНСАТА 17-Т-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 7.6 | 92 |  | 0 | 100 | % | [5 empty] | TS-Q-05:11/ O1010005_U14:3 | TS-Q-05:12/ O1010005_U14:4 |  |  | O1010005:14A/ O1010005_U14:5 | O1010005:14C/ O1010005_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -03022 | 17LZI03022AY |  | AO-NIS (4-20 mA) DCS |  | Сигнал | Loop Powered Indicator | 4124-XZ-DM-21703004 | DCS_AO_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.18 | 17-MC-DCS-006 | TS-Q-05 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010114_U2 | HD5546 | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 2 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-030 Level | УРОВЕНЬ КОНДЕНСАТА В 17-V-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-Q-05:35/ O1010114_U2:3 | TS-Q-05:36/ O1010114_U2:4 |  |  | O1010114:2A/ O1010114_U2:5 | O1010114:2C/ O1010114_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -03042 | 17LT03042 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21703003 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.04 | 17-MC-DCS-006 | TS-O-02 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U7 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-031 Vessel Level | СБОРНИК КОНДЕНСАТА 17-Т-031 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 93 | 94 | 0 | 100 | % | [5 empty] | TS-O-02:7/ O1010002_U7:3 | TS-O-02:8/ O1010002_U7:4 |  |  | O1010002:7A/ O1010002_U7:5 | O1010002:7C/ O1010002_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -03044 | 17LZI03044AY |  | AO-NIS (4-20 mA) DCS |  | Сигнал | Loop Powered Indicator | 4124-XZ-DM-21703003 | DCS_AO_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.19 | 17-MC-DCS-006 | TS-Q-05 | 37 | 38 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010114_U3 | HD5546 | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 3 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-031 Vessel Level | УРОВЕНЬ В БАКЕ ВОЗВРАТНОГО КОНД | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-Q-05:37/ O1010114_U3:3 | TS-Q-05:38/ O1010114_U3:4 |  |  | O1010114:3A/ O1010114_U3:5 | O1010114:3C/ O1010114_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -07034 | 17LT07034 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21707003 | DCS_AI_02 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.06 | 17-MC-DCS-006 | TS-Q-03 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U5 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump basin Level | БАССЕЙН ОВ 17-BS-071 | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 68 | 96 |  | 0 | 100 | % | [5 empty] | TS-Q-03:11/ O1010014R_U5:3 | TS-Q-03:12/ O1010014R_U5:4 |  |  | O1010014R:5A/ O1010014R_U5:5 | O1010014R:5C/ O1010014R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -07034 | 17LY07034A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21707003 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL07 | 12 Pair | Pr.02 | 17-MC-DCS-006 | TS-O-01 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010104R_U10 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 10 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump basin Level | ОХЛ ВОДА В БАССЕЙНЕ 17-BS-071 | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-O-01:3/ O1010104R_U10:3 | TS-O-01:4/ O1010104R_U10:4 |  |  | O1010104R:10A/ O1010104R_U10:5 | O1010104R:10C/ O1010104R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -07061 | 17LT07061 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Radar Level Transmitter- Non Contact Typ | 4124-FY-VD-BD17217L07300001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL07-L073 | 12 Pair | Pr.01 | 17-MC-DCS-006 | TS-Q-02 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011000_U1 | HD5542 | O1011000 | TUA711-AIO16 | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-T-071 92.5% H2SO4 Level | БАК H2SO4 ВОЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 94 | 97 | 0 | 100 | % | [5 empty] | TS-Q-02:1/ O1011000_U1:3 | TS-Q-02:2/ O1011000_U1:4 |  |  | O1011000:1A/ O1011000_U1:5 | O1011000:1C/ O1011000_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -07062 | 17LT07062 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level Transmitter | 4124-FY-VD-BD17217L07300002 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07-L073 | 06 Pair | Pr.01 | 17-MC-DCS-008 | TS-O-04 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011001_U10 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-T-072 Corrosion Inhibitor Level | БАК ИНГИБИТОРА КОРРОЗИИ ВОЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 94 | 97 | 0 | 100 | % | [5 empty] | TS-O-04:1/ O1011001_U10:3 | TS-O-04:2/ O1011001_U10:4 |  |  | O1011001:10A/ O1011001_U10:5 | O1011001:10C/ O1011001_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -07063 | 17LT07063 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level Transmitter | 4124-FY-VD-BD17217L07300003 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL07-L073 | 06 Pair | Pr.01 | 17-MC-DCS-008 | TS-O-07 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011002_U15 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-T-073 Dispersant Level | БАК ДИСПЕРСАНТА ВОЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 94 | 97 | 0 | 100 | % | [5 empty] | TS-O-07:1/ O1011002_U15:3 | TS-O-07:2/ O1011002_U15:4 |  |  | O1011002:15A/ O1011002_U15:5 | O1011002:15C/ O1011002_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -07064 | 17LT07064 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level Transmitter | 4124-FY-VD-BD17217L07300004 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL07-L073 | 06 Pair | Pr.04 | 17-MC-DCS-008 | TS-O-08 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011004_U7 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-T-074 Non-Oxidant Biocide Level | БАК НЕОКСИДАНТА ВОЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 94 | 97 | 0 | 100 | % | [5 empty] | TS-O-08:7/ O1011004_U7:3 | TS-O-08:8/ O1011004_U7:4 |  |  | O1011004:7A/ O1011004_U7:5 | O1011004:7C/ O1011004_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -07065 | 17LT07065 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level Transmitter | 4124-FY-VD-BD17217L07300005 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL07-L073 | 06 Pair | Pr.01 | 17-MC-DCS-008 | TS-O-08 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011004_U6 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-T-075 Chlorine Enhancer Level | БАК БИОЦИДА ПРЕКУРСОРА ВОЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 94 | 97 | 0 | 100 | % | [5 empty] | TS-O-08:1/ O1011004_U6:3 | TS-O-08:2/ O1011004_U6:4 |  |  | O1011004:6A/ O1011004_U6:5 | O1011004:6C/ O1011004_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -07066 | 17LT07066 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level Transmitter | 4124-FY-VD-BD17217L07300006 | DCS_AI_01 | Field |  | 17-C-AD-N-005FL07-L073 | 06 Pair | Pr.01 | 17-MC-DCS-006 | TS-R-02 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011000_U5 | HD5542 | O1011000 | TUA711-AIO16 | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-T-076 12-14% Sodium Hypochlorite Level | БАК ГИПОХЛОРИТА ВОЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 94 | 97 | 0 | 100 | % | [5 empty] | TS-R-02:1/ O1011000_U5:3 | TS-R-02:2/ O1011000_U5:4 |  |  | O1011000:5A/ O1011000_U5:5 | O1011000:5C/ O1011000_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -07075 | 17LT07075 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21707005 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.07 | 17-MC-DCS-006 | TS-Q-03 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U1 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-A-002 CW Pump Basin Level | УРОВЕНЬ В БАССЕЙНЕ 17-BS-071 | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 14.6 | 85.3 | 90.2 | 0 | 100 | % | [5 empty] | TS-Q-03:13/ O1010005_U1:3 | TS-Q-03:14/ O1010005_U1:4 |  |  | O1010005:1A/ O1010005_U1:5 | O1010005:1C/ O1010005_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -07077 | 17LT07077 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21707007 | DCS_AI_01 | Field |  | 17-LT-07077 | 01 Pair | Pr.01 | 17-MC-DCS-006 | TS-O-07 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A | O1010000_U16 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-043 A/B LEVEL | УРОВЕНЬ В БАССЕЙНЕ 17-BS-071 | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 61.5 |  |  | 0 | 100 | % | [5 empty] | TS-O-07:1/ O1010000_U16:3 | TS-O-07:2/ O1010000_U16:4 |  |  | O1010000:16A/ O1010000_U16:5 | O1010000:16C/ O1010000_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -100739 | 17LT100739 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level Transmitter | 4124-GP-VD-BD17917K101004_SH.4 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.11 | 17-MC-DCS-006 | TS-O-03 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010003_U2 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CRANKCASE LUBE OIL LEVEL | МАСЛОБАК 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 30 |  |  | 0 | 100 | % | [5 empty] | TS-O-03:21/ O1010003_U2:3 | TS-O-03:22/ O1010003_U2:4 |  |  | O1010003:2A/ O1010003_U2:5 | O1010003:2C/ O1010003_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -11101 | 17LT11101 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21711101 | DCS_AI_02 | Field |  | 17-C-AD-I-002FL11 | 12 Pair | Pr.01 | 17-MC-DCS-009 | TS-G-02 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010102R_U1 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-U-111 Deaerator storage tank | ДЕАЭРАТОР 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 92 |  | 0 | 100 | % | [5 empty] | TS-G-02:1/ O1010102R_U1:3 | TS-G-02:2/ O1010102R_U1:4 |  |  | O1010102R:1A/ O1010102R_U1:5 | O1010102R:1C/ O1010102R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -11101 | 17LY11101 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21711101 | DCS_AO_02 | Field |  | 17-C-AD-I-002FL11 | 12 Pair | Pr.03 | 17-MC-DCS-009 | TS-G-02 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010110R_U13 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 13 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-U-111 Deaerator storage tank | НАКОПИТ БАК ДЕАЭРАТОРА 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-G-02:5/ O1010110R_U13:3 | TS-G-02:6/ O1010110R_U13:4 |  |  | O1010110R:13A/ O1010110R_U13:5 | O1010110R:13C/ O1010110R_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -11102 | 17LT11102 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21711101 | DCS_AI_02 | Field |  | 17-C-AD-I-002FL11 | 12 Pair | Pr.02 | 17-MC-DCS-009 | TS-G-02 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010102R_U12 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-U-111 Deaerator storage tank | ДЕАЭРАТОР 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 9 | 91 |  | 0 | 100 | % | [5 empty] | TS-G-02:3/ O1010102R_U12:3 | TS-G-02:4/ O1010102R_U12:4 |  |  | O1010102R:12A/ O1010102R_U12:5 | O1010102R:12C/ O1010102R_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -11102 | 17LY11102 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21711101 | DCS_AO_02 | Field |  | 17-C-AD-I-002FL11 | 12 Pair | Pr.04 | 17-MC-DCS-009 | TS-G-02 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010110R_U1 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 1 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-U-111 Deaerator storage tank | НАКОПИТ БАК ДЕАЭРАТОРА 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-G-02:7/ O1010110R_U1:3 | TS-G-02:8/ O1010110R_U1:4 |  |  | O1010110R:1A/ O1010110R_U1:5 | O1010110R:1C/ O1010110R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -113500 | 17LT113500 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.03 | 17-MC-DCS-006 | TS-O-05 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U1 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM DRUM LEVEL 17-L-111-V-111 | БАРАБАН ПУСКОВОГО КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 31 |  |  | 0 | 100.0 | % | [5 empty] | TS-O-05:5/ O1010014R_U1:3 | TS-O-05:6/ O1010014R_U1:4 |  |  | O1010014R:1A/ O1010014R_U1:5 | O1010014R:1C/ O1010014R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -113500 | 17LY113500A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | LY - Smart Positioner (General) | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.14 | 17-MC-DCS-008 | TS-P-02 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010108R_U7 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 7 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM DRUM LEVEL 17-L-111-V-111 | УРОВЕНЬ В БАРАБАНЕ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-P-02:27/ O1010108R_U7:3 | TS-P-02:28/ O1010108R_U7:4 |  |  | O1010108R:7A/ O1010108R_U7:5 | O1010108R:7C/ O1010108R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -113500 | 17LY113500B |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | LY - Smart Positioner (General) | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.15 | 17-MC-DCS-008 | TS-P-02 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010108R_U8 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 8 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM DRUM LEVEL 17-L-111-V-111 | УРОВЕНЬ В БАРАБАНЕ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-P-02:29/ O1010108R_U8:3 | TS-P-02:30/ O1010108R_U8:4 |  |  | O1010108R:8A/ O1010108R_U8:5 | O1010108R:8C/ O1010108R_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -113704 | 17LT113704 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | DP Level Transmitter | 4124-FB-VD-BD00317L11111309 | DCS_AI_01 | Field |  | 17-C-AD-N-702FL11-L111 | 06 Pair | Pr.04 | 17-MC-DCS-006 | TS-Q-06 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010006_U14 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Rundown Tank Level 17-L-111-T-114 | БАК ВЫБЕГА ДУТЬЕВОГО ВЕНТ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100.0 | % | [5 empty] | TS-Q-06:7/ O1010006_U14:3 | TS-Q-06:8/ O1010006_U14:4 |  |  | O1010006:14A/ O1010006_U14:5 | O1010006:14C/ O1010006_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -11503 | 17LT11503 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level Transmitter | 4124-FY-VD-BD17117L11200001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.01 | 17-MC-DCS-006 | TS-R-01 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010004_U5 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-T-001 Sodium Phosphate Level | БАК ФОСФАТОВ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | 3 | 6 |  |  | 0 | 100 | % | [5 empty] | TS-R-01:1/ O1010004_U5:3 | TS-R-01:2/ O1010004_U5:4 |  |  | O1010004:5A/ O1010004_U5:5 | O1010004:5C/ O1010004_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -11504 | 17LT11504 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | DP Level Transmitter | 4124-FY-VD-BD17117L11300001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.02 | 17-MC-DCS-006 | TS-R-01 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010004_U6 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-113-T-001 Oxygen Scavenger Level | БАК ПОГЛОТИТЕЛЯ КИСЛОРОДА КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | 3 | 6 |  |  | 0 | 100 | % | [5 empty] | TS-R-01:3/ O1010004_U6:3 | TS-R-01:4/ O1010004_U6:4 |  |  | O1010004:6A/ O1010004_U6:5 | O1010004:6C/ O1010004_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -11505 | 17LT11505 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Level Transmitter | 4124-FY-VD-BD17117L11400001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.03 | 17-MC-DCS-006 | TS-R-01 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010004_U7 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-114-T-001 Amine Level | БАК АМИНОВ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | 3 | 6 |  |  | 0 | 100 | % | [5 empty] | TS-R-01:5/ O1010004_U7:3 | TS-R-01:6/ O1010004_U7:4 |  |  | O1010004:7A/ O1010004_U7:5 | O1010004:7C/ O1010004_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -11700 | 17LT11700 |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21711701 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL11 | 12 Pair | Pr.01 | 17-MC-DCS-006 | TS-O-04 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010012R_U14 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-111 Level | БАРАБАН ПРОДУВОК 17-V-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | 17-LI-11700 | 17-LI-11701 | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 62 |  | 0 | 100 | % | [5 empty] | TS-O-04:1/ O1010012R_U14:3 | TS-O-04:2/ O1010012R_U14:4 |  |  | O1010012R:14A/ O1010012R_U14:5 | O1010012R:14C/ O1010012R_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -11700 | 17LY11700 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21711701 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL11 | 12 Pair | Pr.03 | 17-MC-DCS-006 | TS-O-04 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010106R_U2 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 2 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-111 Level | ПРОДУВ ПАРОВОЙ БАРАБАН 17-V-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-O-04:5/ O1010106R_U2:3 | TS-O-04:6/ O1010106R_U2:4 |  |  | O1010106R:2A/ O1010106R_U2:5 | O1010106R:2C/ O1010106R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -11701 | 17LT11701 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21711701 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11 | 12 Pair | Pr.02 | 17-MC-DCS-006 | TS-O-04 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010003_U6 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-111 Level | БАРАБАН ПРОДУВОК 17-V-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  | 87.2 | 0 | 100 | % | [5 empty] | TS-O-04:3/ O1010003_U6:3 | TS-O-04:4/ O1010003_U6:4 |  |  | O1010003:6A/ O1010003_U6:5 | O1010003:6C/ O1010003_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -13002 | 17LT13002 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21713001 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.05 | 17-MC-DCS-006 | TS-O-02 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U14 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-131 Level | БАК ПИТЬЕВОЙ ВОДЫ 17-V-131 | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | 17-LI-13002 | 17-LZI-13003 | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 20 | 95 |  | 0 | 100 | % | [5 empty] | TS-O-02:9/ O1010014R_U14:3 | TS-O-02:10/ O1010014R_U14:4 |  |  | O1010014R:14A/ O1010014R_U14:5 | O1010014R:14C/ O1010014R_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -13002 | 17LY13002 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21713001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.07 | 17-MC-DCS-006 | TS-O-02 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011012R_U4 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 4 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-131 Level | 17-V-131 УРОВЕНЬ В БАКЕ ВОДЫ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-O-02:13/ O1011012R_U4:3 | TS-O-02:14/ O1011012R_U4:4 |  |  | O1011012R:4A/ O1011012R_U4:5 | O1011012R:4C/ O1011012R_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -14002 | 17LT14002 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21714001 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL14 | 12 Pair | Pr.01 | 17-MC-DCS-008 | TS-O-05 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011001_U12 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-BS-143A/B First Flush Basins | УРОВЕНЬ В СБОРНИКЕ 17-BS-143A/B | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6 | 70 | 85.2 | 0 | 100 | % | [5 empty] | TS-O-05:1/ O1011001_U12:3 | TS-O-05:2/ O1011001_U12:4 |  |  | O1011001:12A/ O1011001_U12:5 | O1011001:12C/ O1011001_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -140025 | 17LT140025 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21714003 | DCS_AI_01 | Field |  | 17-LT-140025 | 01 Pair | Pr.01 | 17-MC-DCS-009 | TS-G-06 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A | O1011005_U11 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-140 Level | УРОВЕНЬ КНС ЛИВНЕВЫХ СТОКОВ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 6.25 | 77.5 | 100 | 0 | 100 | % | [5 empty] | TS-G-06:1/ O1011005_U11:3 | TS-G-06:2/ O1011005_U11:4 |  |  | O1011005:11A/ O1011005_U11:5 | O1011005:11C/ O1011005_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -140028 | 17LT140028 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21714003 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL14 | 12 Pair | Pr.06 | 17-MC-DCS-008 | TS-O-05 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011002_U12 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-143 Level | УРОВЕНЬ КНС ЛИВНЕВЫХ СТОКОВ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 12.5 | 75 | 100 | 0 | 100 | % | [5 empty] | TS-O-05:11/ O1011002_U12:3 | TS-O-05:12/ O1011002_U12:4 |  |  | O1011002:12A/ O1011002_U12:5 | O1011002:12C/ O1011002_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -140031 | 17LT140031 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21714003 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL14 | 12 Pair | Pr.07 | 17-MC-DCS-008 | TS-O-05 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011002_U13 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-146 Level | УРОВЕНЬ КНС ГРЯЗНЫХ СТОКОВ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 4 | 72 | 90 | 0 | 100 | % | [5 empty] | TS-O-05:13/ O1011002_U13:3 | TS-O-05:14/ O1011002_U13:4 |  |  | O1011002:13A/ O1011002_U13:5 | O1011002:13C/ O1011002_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-L -140034 | 17LT140034 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21714003 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL14 | 12 Pair | Pr.08 | 17-MC-DCS-008 | TS-O-05 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011002_U14 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-147 Level | УРОВЕНЬ КНС МАСЛОЗАГР СТОКОВ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 7.9 | 76.2 | 100 | 0 | 100 | % | [5 empty] | TS-O-05:15/ O1011002_U14:3 | TS-O-05:16/ O1011002_U14:4 |  |  | O1011002:14A/ O1011002_U14:5 | O1011002:14C/ O1011002_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -14006 | 17LT14006 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21714002 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL14 | 12 Pair | Pr.02 | 17-MC-DCS-008 | TS-O-05 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011001_U13 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-BS-144 Rain Water Retention Basin | BS-144 СБОРНИК ЛИВНЕВЫХ ВОД | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 14.2 | 80.9 | 90.5 | 0 | 100 | % | [5 empty] | TS-O-05:3/ O1011001_U13:3 | TS-O-05:4/ O1011001_U13:4 |  |  | O1011001:13A/ O1011001_U13:5 | O1011001:13C/ O1011001_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -14022 | 17LT14022 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21714002 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL14 | 12 Pair | Pr.03 | 17-MC-DCS-008 | TS-O-05 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011001_U14 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-BS-144 Rain Water Retention Basin | BS-145 СБОРНИК ЛИВНЕВЫХ ВОД | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 21.7 | 82.6 | 91.3 | 0 | 100 | % | [5 empty] | TS-O-05:5/ O1011001_U14:3 | TS-O-05:6/ O1011001_U14:4 |  |  | O1011001:14A/ O1011001_U14:5 | O1011001:14C/ O1011001_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -17101 | 17LT17101 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21717101 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.04 | 17-MC-DCS-008 | TS-O-02 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011001_U4 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-171 Glycol water expansion vessel | РАСШ БАК ГЛИКОЛИВОЙ ВОДЫ 17-V-171 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 13.2 | 70.6 |  | 0 | 100 | % | [5 empty] | TS-O-02:7/ O1011001_U4:3 | TS-O-02:8/ O1011001_U4:4 |  |  | O1011001:4A/ O1011001_U4:5 | O1011001:4C/ O1011001_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-L -17102 | 17LT17102 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21717101 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.05 | 17-MC-DCS-008 | TS-O-02 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011001_U5 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-172 Glycol water storage drum | БАК ГЛИКОЛИВОЙ ВОДЫ 17-V-172 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 20.8 | 91.7 |  | 0 | 100 | % | [5 empty] | TS-O-02:9/ O1011001_U5:3 | TS-O-02:10/ O1011001_U5:4 |  |  | O1011001:5A/ O1011001_U5:5 | O1011001:5C/ O1011001_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 | 17-L-152 | 17XL15001 |  | DI-NIS (Thermistors PTC) DCS | 30.05.2024 добавлен по TQ_ALL_055 | Сигнал |  |  | DCS_DI_02 |  |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.17 | 17-MC-DCS-002 | TS-O-08 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U28 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-152 | Установка 17-L-152 в работе | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | RUNNING | NOT RUNNING | [13 empty] | TS-O-08:33/ O1011104_U28:3 | TS-O-08:34/ O1011104_U28:4 |  |  | O1011104:28A/ O1011104_U28:5 | O1011104:28B/ O1011104_U28:6 | [6 empty] | 28A | 28B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 | 17-L-152 | 17XLA15001 |  | DI-NIS (Thermistors PTC) DCS | 30.05.2024 добавлен по TQ_ALL_055 | Сигнал |  |  | DCS_DI_02 |  |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.18 | 17-MC-DCS-002 | TS-O-08 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U29 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-152 | Установка 17-L-152 авария | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | FAULT | NORMAL | [13 empty] | TS-O-08:35/ O1011104_U29:3 | TS-O-08:36/ O1011104_U29:4 |  |  | O1011104:29A/ O1011104_U29:5 | O1011104:29B/ O1011104_U29:6 | [6 empty] | 29A | 29B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 | 17-L-181 | 17XL15005 |  | DI-NIS (Thermistors PTC) DCS | 30.05.2024 добавлен по TQ_ALL_055 | Сигнал |  |  | DCS_DI_02 |  |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.19 | 17-MC-DCS-002 | TS-O-08 | 37 | 38 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U30 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-181 | Установка 17-L-181 в работе | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | RUNNING | NOT RUNNING | [13 empty] | TS-O-08:37/ O1011104_U30:3 | TS-O-08:38/ O1011104_U30:4 |  |  | O1011104:30A/ O1011104_U30:5 | O1011104:30B/ O1011104_U30:6 | [6 empty] | 30A | 30B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 | 17-L-181 | 17XLA15005 |  | DI-NIS (Thermistors PTC) DCS | 30.05.2024 добавлен по TQ_ALL_055 | Сигнал |  |  | DCS_DI_02 |  |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.20 | 17-MC-DCS-002 | TS-O-08 | 39 | 40 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U31 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-181 | Установка 17-L-181 авария | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | FAULT | NORMAL | [13 empty] | TS-O-08:39/ O1011104_U31:3 | TS-O-08:40/ O1011104_U31:4 |  |  | O1011104:31A/ O1011104_U31:5 | O1011104:31B/ O1011104_U31:6 | [6 empty] | 31A | 31B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -A | 17XSM001LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.01 | 17-MC-DCS-005 | TS-G-01 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001A | K001A ВОЗДУХОДУВКА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:1/ O1011111:1A | TS-G-01:2/ O1011111:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -A | 17XSAM001LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.02 | 17-MC-DCS-005 | TS-G-01 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001A | 17L022K001A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:3/ O1011111:2A | TS-G-01:4/ O1011111:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -A | 17XSRM001LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.03 | 17-MC-DCS-005 | TS-G-01 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001A | 17L022K001A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:5/ O1011111:3A | TS-G-01:6/ O1011111:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -A | 17XYSPM001LKA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.01 | 17-MC-DCS-005 | TS-H-01 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001A | 17L022K001A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:2/ O1011209:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -A | 17XYSTM001LKA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.03 | 17-MC-DCS-005 | TS-H-01 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001A | 17L022K001A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:4/ O1011209:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -B | 17XSM001LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.01 | 17-MC-DCS-005 | TS-G-02 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001B | K001B ВОЗДУХОДУВКА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:1/ O1011111:14A | TS-G-02:2/ O1011111:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -B | 17XSAM001LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.02 | 17-MC-DCS-005 | TS-G-02 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001B | 17L022K001B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:3/ O1011111:15A | TS-G-02:4/ O1011111:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -B | 17XSRM001LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.03 | 17-MC-DCS-005 | TS-G-02 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001B | 17L022K001B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:5/ O1011111:16A | TS-G-02:6/ O1011111:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -B | 17XYSPM001LKB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.05 | 17-MC-DCS-005 | TS-H-01 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001B | 17L022K001B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:6/ O1011209:3A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0001LK -B | 17XYSTM001LKB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.07 | 17-MC-DCS-005 | TS-H-01 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-001B | 17L022K001B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:8/ O1011209:4A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -A | 17XSM002LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.04 | 17-MC-DCS-005 | TS-G-02 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002A | K002A ВОЗДУХОДУВКА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:7/ O1011111:17A | TS-G-02:8/ O1011111:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -A | 17XSAM002LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.05 | 17-MC-DCS-005 | TS-G-02 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002A | 17L022K002A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:9/ O1011111:18A | TS-G-02:10/ O1011111:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -A | 17XSRM002LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.06 | 17-MC-DCS-005 | TS-G-02 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002A | 17L022K002A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:11/ O1011111:19A | TS-G-02:12/ O1011111:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -A | 17XYSPM002LKA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.01 | 17-MC-DCS-004 | TS-P-02 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002A | 17L022K002A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:2/ O1011207:25A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -A | 17XYSTM002LKA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.03 | 17-MC-DCS-004 | TS-P-02 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002A | 17L022K002A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:4/ O1011207:26A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -B | 17XSM002LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.07 | 17-MC-DCS-005 | TS-G-02 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002B | K002B ВОЗДУХОДУВКА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:13/ O1011111:20A | TS-G-02:14/ O1011111:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -B | 17XSAM002LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.08 | 17-MC-DCS-005 | TS-G-02 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002B | 17L022K002B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:15/ O1011111:21A | TS-G-02:16/ O1011111:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -B | 17XSRM002LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.09 | 17-MC-DCS-005 | TS-G-02 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002B | 17L022K002B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:17/ O1011111:22A | TS-G-02:18/ O1011111:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -B | 17XYSPM002LKB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.05 | 17-MC-DCS-004 | TS-P-02 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002B | 17L022K002B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:6/ O1011207:27A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0002LK -B | 17XYSTM002LKB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.07 | 17-MC-DCS-004 | TS-P-02 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Blower 17-L-022-K-002B | 17L022K002B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:8/ O1011207:28A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -A | 17XSM021LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.16 | 17-MC-DCS-005 | TS-G-03 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | P021A НАСОС ПЕРЕКАЧКИ NAOH | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:31/ O1011112:26A | TS-G-03:32/ O1011112:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -A | 17XSAM021LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.17 | 17-MC-DCS-005 | TS-G-03 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | L022P021A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:33/ O1011112:27A | TS-G-03:34/ O1011112:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -A | 17XSRM021LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.18 | 17-MC-DCS-005 | TS-G-03 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | L022P021A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:35/ O1011112:28A | TS-G-03:36/ O1011112:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -A | 17XYSPM021LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.09 | 17-MC-DCS-005 | TS-H-03 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | L022P021A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:10/ O1011209:29A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -A | 17XYSTM021LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.11 | 17-MC-DCS-005 | TS-H-03 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | L022P021A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:12/ O1011209:30A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -B | 17XSM021LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.19 | 17-MC-DCS-005 | TS-G-03 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | P021B НАСОС ПЕРЕКАЧКИ NAOH | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:37/ O1011112:29A | TS-G-03:38/ O1011112:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -B | 17XSAM021LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.20 | 17-MC-DCS-005 | TS-G-03 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | L022P021B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:39/ O1011112:30A | TS-G-03:40/ O1011112:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -B | 17XSRM021LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.21 | 17-MC-DCS-005 | TS-G-03 | 41 | 42 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | L022P021B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:41/ O1011112:31A | TS-G-03:42/ O1011112:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -B | 17XYSPM021LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.13 | 17-MC-DCS-005 | TS-H-03 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | L022P021B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:14/ O1011209:31A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0021LP -B | 17XYSTM021LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.15 | 17-MC-DCS-005 | TS-H-03 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-021A | L022P021B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:16/ O1011209:32A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -A | 17XSM022LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.10 | 17-MC-DCS-005 | TS-G-01 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-022A | P022A НАСОС H2SO4 ФСД | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:19/ O1011111:10A | TS-G-01:20/ O1011111:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -A | 17XSAM022LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.11 | 17-MC-DCS-005 | TS-G-01 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-022A | L022P022A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:21/ O1011111:11A | TS-G-01:22/ O1011111:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -A | 17XSRM022LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.19 | 17-MC-DCS-005 | TS-G-02 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-022A | L022P022A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:37/ O1011111:32A | TS-G-02:38/ O1011111:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -A | 17XYSPM022LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.05 | 17-MC-DCS-005 | TS-H-02 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-022A | L022P022A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:6/ O1011209:15A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -A | 17XYSTM022LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.07 | 17-MC-DCS-005 | TS-H-02 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-022A | L022P022A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:8/ O1011209:16A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -B | 17XSM022LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.01 | 17-MC-DCS-005 | TS-G-03 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-022B | P022B НАСОС H2SO4 ФСД | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:1/ O1011112:11A | TS-G-03:2/ O1011112:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -B | 17XSAM022LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.02 | 17-MC-DCS-005 | TS-G-03 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-022B | L022P022B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:3/ O1011112:12A | TS-G-03:4/ O1011112:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -B | 17XSRM022LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.03 | 17-MC-DCS-005 | TS-G-03 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-022B | L022P022B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:5/ O1011112:13A | TS-G-03:6/ O1011112:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -B | 17XYSPM022LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.09 | 17-MC-DCS-005 | TS-H-02 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-022B | L022P022B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:10/ O1011209:17A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0022LP -B | 17XYSTM022LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.11 | 17-MC-DCS-005 | TS-H-02 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028B | L022P022B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:12/ O1011209:18A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -A | 17XSM023LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.04 | 17-MC-DCS-005 | TS-G-03 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023A | P023A НАСОС НЕЙТРАЛИЗАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:7/ O1011112:14A | TS-G-03:8/ O1011112:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -A | 17XSAM023LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.05 | 17-MC-DCS-005 | TS-G-03 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023A | L022P023A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:9/ O1011112:15A | TS-G-03:10/ O1011112:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -A | 17XSRM023LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.06 | 17-MC-DCS-005 | TS-G-03 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023A | L022P023A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:11/ O1011112:16A | TS-G-03:12/ O1011112:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -A | 17XYSPM023LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.13 | 17-MC-DCS-005 | TS-H-02 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023A | L022P023A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:14/ O1011209:19A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -A | 17XYSTM023LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.15 | 17-MC-DCS-005 | TS-H-02 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023A | L022P023A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:16/ O1011209:20A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -B | 17XSM023LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.07 | 17-MC-DCS-005 | TS-G-03 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023B | P023B НАСОС НЕЙТРАЛИЗАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:13/ O1011112:17A | TS-G-03:14/ O1011112:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -B | 17XSAM023LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.08 | 17-MC-DCS-005 | TS-G-03 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023B | L022P023B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:15/ O1011112:18A | TS-G-03:16/ O1011112:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -B | 17XSRM023LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.09 | 17-MC-DCS-005 | TS-G-03 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023B | L022P023B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:17/ O1011112:19A | TS-G-03:18/ O1011112:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -B | 17XYSPM023LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.17 | 17-MC-DCS-005 | TS-H-02 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023B | L022P023B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:18/ O1011209:21A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0023LP -B | 17XYSTM023LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.19 | 17-MC-DCS-005 | TS-H-02 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-023B | L022P023B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:20/ O1011209:22A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -A | 17XSM024LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.13 | 17-MC-DCS-004 | TS-R-04 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024A | P024A НАСОС РЕГ. СТОКА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:25/ O1011110:7A | TS-R-04:26/ O1011110:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -A | 17XSAM024LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.14 | 17-MC-DCS-004 | TS-R-04 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024A | L022P024A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:27/ O1011110:8A | TS-R-04:28/ O1011110:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -A | 17XSRM024LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.15 | 17-MC-DCS-004 | TS-R-04 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024A | L022P024A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:29/ O1011110:9A | TS-R-04:30/ O1011110:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -A | 17XYSPM024LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.01 | 17-MC-DCS-004 | TS-P-01 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024A | L022P024A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:2/ O1011207:15A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -A | 17XYSTM024LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.03 | 17-MC-DCS-004 | TS-P-01 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024A | L022P024A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:4/ O1011207:16A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -B | 17XSM024LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.16 | 17-MC-DCS-004 | TS-R-04 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024B | P024B НАСОС РЕГ. СТОКА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:31/ O1011110:10A | TS-R-04:32/ O1011110:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -B | 17XSAM024LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.17 | 17-MC-DCS-004 | TS-R-04 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024B | L022P024B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:33/ O1011110:11A | TS-R-04:34/ O1011110:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -B | 17XSRM024LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.18 | 17-MC-DCS-004 | TS-R-04 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024B | L022P024B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:35/ O1011110:12A | TS-R-04:36/ O1011110:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -B | 17XYSPM024LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.17 | 17-MC-DCS-004 | TS-P-02 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024B | L022P024B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:18/ O1011208:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0024LP -B | 17XYSTM024LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.19 | 17-MC-DCS-004 | TS-P-02 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-024B | L022P024B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:20/ O1011208:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -A | 17XSM025LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.19 | 17-MC-DCS-004 | TS-R-04 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025A | P025A НАСОС РЕГ. СТОКА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:37/ O1011110:13A | TS-R-04:38/ O1011110:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -A | 17XSAM025LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.20 | 17-MC-DCS-004 | TS-R-04 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025A | L022P025A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:39/ O1011110:14A | TS-R-04:40/ O1011110:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -A | 17XSRM025LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.21 | 17-MC-DCS-004 | TS-R-04 | 41 | 42 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025A | L022P025A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:41/ O1011110:15A | TS-R-04:42/ O1011110:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -A | 17XYSPM025LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.05 | 17-MC-DCS-004 | TS-P-01 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025A | L022P025A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:6/ O1011207:17A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -A | 17XYSTM025LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.07 | 17-MC-DCS-004 | TS-P-01 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025A | L022P025A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:8/ O1011207:18A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -B | 17XSM025LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-016BL02 | 12 Pair | Pr.01 | 17-MC-DCS-004 | TS-P-06 | 1 | 2 |  | 24 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025B | P025B НАСОС РЕГ. СТОКА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-06:1/ O1011110:16A | TS-P-06:2/ O1011110:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -B | 17XSAM025LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-016BL02 | 12 Pair | Pr.02 | 17-MC-DCS-004 | TS-P-06 | 3 | 4 |  | 24 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025B | L022P025B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-06:3/ O1011110:17A | TS-P-06:4/ O1011110:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -B | 17XSRM025LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_03 | MCC |  | 17-I-DD-N-016BL02 | 12 Pair | Pr.03 | 17-MC-DCS-004 | TS-P-06 | 5 | 6 |  | 24 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025B | L022P025B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-06:5/ O1011110:18A | TS-P-06:6/ O1011110:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -B | 17XYSPM025LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.21 | 17-MC-DCS-004 | TS-P-02 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025B | L022P025B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:22/ O1011208:3A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0025LP -B | 17XYSTM025LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.23 | 17-MC-DCS-004 | TS-P-02 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization pump 17-L-022-P-025B | L022P025B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:24/ O1011208:4A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -A | 17XYSPM026LPA |  | DO-NIS (MCC 230VAC) DCS | Переподключены с платы O1011213 (14.06.2024) | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.17 | 17-MC-DCS-005 | TS-H-03 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026A | L022P026A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:18/ O1010215:9A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -A | 17XYSTM026LPA |  | DO-NIS (MCC 230VAC) DCS | Переподключены с платы O1011213 (14.06.2024) | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.19 | 17-MC-DCS-005 | TS-H-03 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026A | L022P026A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:20/ O1010215:10A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -A | 17XSM026LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.01 | 17-MC-DCS-004 | TS-R-04 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026A | P026A НАСОС NAOH ФСД | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:1/ O1011109:27A | TS-R-04:2/ O1011109:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -A | 17XSAM026LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.02 | 17-MC-DCS-004 | TS-R-04 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026A | L022P026A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:3/ O1011109:28A | TS-R-04:4/ O1011109:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -A | 17XSRM026LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.03 | 17-MC-DCS-004 | TS-R-04 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026A | L022P026A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:5/ O1011109:29A | TS-R-04:6/ O1011109:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -B | 17XSM026LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.04 | 17-MC-DCS-004 | TS-R-04 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026B | P026B НАСОС NAOH ФСД | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:7/ O1011109:30A | TS-R-04:8/ O1011109:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -B | 17XSAM026LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.05 | 17-MC-DCS-004 | TS-R-04 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026B | L022P026B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:9/ O1011109:31A | TS-R-04:10/ O1011109:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -B | 17XSRM026LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.06 | 17-MC-DCS-004 | TS-R-04 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026B | L022P026B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:11/ O1011109:32A | TS-R-04:12/ O1011109:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -B | 17XYSPM026LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.09 | 17-MC-DCS-004 | TS-P-02 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026B | L022P026B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:10/ O1011207:29A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0026LP -B | 17XYSTM026LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.11 | 17-MC-DCS-004 | TS-P-02 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-026B | L022P026B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:12/ O1011207:30A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -A | 17XYSPM027LPA |  | DO-NIS (MCC 230VAC) DCS | Переподключены с платы O1011213 (14.06.2024) | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.21 | 17-MC-DCS-005 | TS-H-03 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027A | L022P027A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:22/ O1010215:11A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -A | 17XYSTM027LPA |  | DO-NIS (MCC 230VAC) DCS | Переподключены с платы O1011213 (14.06.2024) | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.23 | 17-MC-DCS-005 | TS-H-03 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027A | L022P027A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:24/ O1010215:12A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -A | 17XSM027LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.07 | 17-MC-DCS-004 | TS-R-04 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027A | P027A НАСОС NAOH, НЕЙТРАЛИЗАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:13/ O1011110:1A | TS-R-04:14/ O1011110:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -A | 17XSAM027LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.08 | 17-MC-DCS-004 | TS-R-04 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027A | L022P027A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:15/ O1011110:2A | TS-R-04:16/ O1011110:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -A | 17XSRM027LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.09 | 17-MC-DCS-004 | TS-R-04 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027A | L022P027A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:17/ O1011110:3A | TS-R-04:18/ O1011110:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -B | 17XSM027LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.10 | 17-MC-DCS-004 | TS-R-04 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027B | P027A НАСОС NAOH, НЕЙТРАЛИЗАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:19/ O1011110:4A | TS-R-04:20/ O1011110:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -B | 17XSAM027LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.11 | 17-MC-DCS-004 | TS-R-04 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027B | L022P027B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:21/ O1011110:5A | TS-R-04:22/ O1011110:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -B | 17XSRM027LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DI_03 | MCC |  | 17-I-DD-N-015BL02 | 24 Pair | Pr.12 | 17-MC-DCS-004 | TS-R-04 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027B | L022P027B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-04:23/ O1011110:6A | TS-R-04:24/ O1011110:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -B | 17XYSPM027LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.13 | 17-MC-DCS-004 | TS-P-02 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027B | L022P027B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:14/ O1011207:31A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0027LP -B | 17XYSTM027LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_DO_03 | MCC |  | 17-I-CD-N-016BL02 | 30 Core | C.15 | 17-MC-DCS-004 | TS-P-02 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH unloading pump 17-L-022-P-027B | L022P027B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-02:16/ O1011207:32A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -A | 17XSM028LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.10 | 17-MC-DCS-005 | TS-G-03 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028A | P028A НАСОС РЕГЕНЕРАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:19/ O1011112:20A | TS-G-03:20/ O1011112:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -A | 17XSAM028LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.11 | 17-MC-DCS-005 | TS-G-03 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028A | L022P028A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:21/ O1011112:21A | TS-G-03:22/ O1011112:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -A | 17XSRM028LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.12 | 17-MC-DCS-005 | TS-G-03 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028A | L022P028A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:23/ O1011112:22A | TS-G-03:24/ O1011112:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -A | 17XYSPM028LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.21 | 17-MC-DCS-005 | TS-H-02 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028A | L022P028A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:22/ O1011209:23A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -A | 17XYSTM028LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.23 | 17-MC-DCS-005 | TS-H-02 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028A | L022P028A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:24/ O1011209:24A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -B | 17XSM028LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.13 | 17-MC-DCS-005 | TS-G-03 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028B | P028B НАСОС РЕГЕНЕРАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:25/ O1011112:23A | TS-G-03:26/ O1011112:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -B | 17XSAM028LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.14 | 17-MC-DCS-005 | TS-G-03 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028B | L022P028B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:27/ O1011112:24A | TS-G-03:28/ O1011112:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -B | 17XSRM028LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DI_03 | MCC |  | 17-I-DD-N-014BL02 | 24 Pair | Pr.15 | 17-MC-DCS-005 | TS-G-03 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028B | L022P028B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:29/ O1011112:25A | TS-G-03:30/ O1011112:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -B | 17XYSPM028LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.01 | 17-MC-DCS-005 | TS-H-03 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028B | L022P028B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:2/ O1011209:25A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0028LP -B | 17XYSTM028LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.5 | DCS_DO_03 | MCC |  | 17-I-CD-N-003BL02 | 30 Core | C.03 | 17-MC-DCS-005 | TS-H-03 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 Dosing pump 17-L-022-P-028B | L022P028B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-03:4/ O1011209:26A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -A | 17XSM029LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.04 | 17-MC-DCS-005 | TS-G-01 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029A | P029A НАСОС ПРОМЫВКИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:7/ O1011111:4A | TS-G-01:8/ O1011111:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -A | 17XSAM029LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.05 | 17-MC-DCS-005 | TS-G-01 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029A | 17L022P029A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:9/ O1011111:5A | TS-G-01:10/ O1011111:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -A | 17XSRM029LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.06 | 17-MC-DCS-005 | TS-G-01 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029A | 17L022P029A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:11/ O1011111:6A | TS-G-01:12/ O1011111:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -A | 17XYSPM029LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.09 | 17-MC-DCS-005 | TS-H-01 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029A | 17L022P029A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:10/ O1011209:5A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -A | 17XYSTM029LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.11 | 17-MC-DCS-005 | TS-H-01 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029A | 17L022P029A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:12/ O1011209:6A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -B | 17XSM029LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.10 | 17-MC-DCS-005 | TS-G-02 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029B | P029B НАСОС ПРОМЫВКИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:19/ O1011111:23A | TS-G-02:20/ O1011111:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -B | 17XSAM029LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.11 | 17-MC-DCS-005 | TS-G-02 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029B | 17L022P029B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:21/ O1011111:24A | TS-G-02:22/ O1011111:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -B | 17XSRM029LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.12 | 17-MC-DCS-005 | TS-G-02 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029B | 17L022P029B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:23/ O1011111:25A | TS-G-02:24/ O1011111:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -B | 17XYSPM029LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.13 | 17-MC-DCS-005 | TS-H-01 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029B | 17L022P029B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:14/ O1011209:7A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0029LP -B | 17XYSTM029LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.15 | 17-MC-DCS-005 | TS-H-01 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rinse Pump 17-L-022-P-029B | 17L022P029B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:16/ O1011209:8A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -A | 17XSM033LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.07 | 17-MC-DCS-005 | TS-G-01 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-A | P033A НАСОС РЕГЕНЕРАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:13/ O1011111:7A | TS-G-01:14/ O1011111:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -A | 17XSAM033LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.08 | 17-MC-DCS-005 | TS-G-01 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-A | 17L022P033A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:15/ O1011111:8A | TS-G-01:16/ O1011111:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -A | 17XSRM033LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.09 | 17-MC-DCS-005 | TS-G-01 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-A | 17L022P033A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:17/ O1011111:9A | TS-G-01:18/ O1011111:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -A | 17XYSPM033LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.17 | 17-MC-DCS-005 | TS-H-01 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-A | 17L022P033A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:18/ O1011209:9A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -A | 17XYSTM033LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.19 | 17-MC-DCS-005 | TS-H-01 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-A | 17L022P033A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:20/ O1011209:10A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -B | 17XSM033LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.13 | 17-MC-DCS-005 | TS-G-02 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-B | P033B НАСОС РЕГЕНЕРАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:25/ O1011111:26A | TS-G-02:26/ O1011111:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -B | 17XSAM033LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.14 | 17-MC-DCS-005 | TS-G-02 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-B | 17L022P033B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:27/ O1011111:27A | TS-G-02:28/ O1011111:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -B | 17XSRM033LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.15 | 17-MC-DCS-005 | TS-G-02 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-B | 17L022P033B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:29/ O1011111:28A | TS-G-02:30/ O1011111:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -B | 17XYSPM033LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.21 | 17-MC-DCS-005 | TS-H-01 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-B | 17L022P033B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:22/ O1011209:11A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -B | 17XYSTM033LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-001BL02 | 30 Core | C.23 | 17-MC-DCS-005 | TS-H-01 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-B | 17L022P033B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-01:24/ O1011209:12A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -C | 17XSM033LPC |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.16 | 17-MC-DCS-005 | TS-G-02 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-C | P033C НАСОС РЕГЕНЕРАЦИИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:31/ O1011111:29A | TS-G-02:32/ O1011111:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -C | 17XSAM033LPC |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.17 | 17-MC-DCS-005 | TS-G-02 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-C | 17L022P033C ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:33/ O1011111:30A | TS-G-02:34/ O1011111:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -C | 17XSRM033LPC |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-013BL02 | 24 Pair | Pr.18 | 17-MC-DCS-005 | TS-G-02 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011111 | TUA711-DIO32 | 17-SC-DCS-002/O1011111/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011111 | 12 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-C | 17L022P033C МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:35/ O1011111:31A | TS-G-02:36/ O1011111:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -C | 17XYSPM033LPC |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.01 | 17-MC-DCS-005 | TS-H-02 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-C | 17L022P033C ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:2/ O1011209:13A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -0033LP -C | 17XYSTM033LPC |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17617L02200002_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-002BL02 | 30 Core | C.03 | 17-MC-DCS-005 | TS-H-02 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011209 | TUA711-DIO32 | 17-SC-DCS-002/O1011209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011209 | 10 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Regeneration Pump 17-L-022-P-033-C | 17L022P033C ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-02:4/ O1011209:14A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL112 | 17XSM01AL112 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17117L11200001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.01 | 17-MC-DCS-004 | TS-O-05 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001A Sodium Phosphate Injection Pump | 112P001A НАСОС ПОДАЧИ ФОСФАТОВ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:1/ O1011106:1A | TS-O-05:2/ O1011106:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL112 | 17XSAM01AL112 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17117L11200001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.02 | 17-MC-DCS-004 | TS-O-05 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001A Sodium Phosphate Injection Pump | 17L112P001A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:3/ O1011106:2A | TS-O-05:4/ O1011106:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL112 | 17XSRM01AL112 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17117L11200001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.03 | 17-MC-DCS-004 | TS-O-05 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001A Sodium Phosphate Injection Pump | 17L112P001A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:5/ O1011106:3A | TS-O-05:6/ O1011106:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL112 | 17XYSTM01AL112 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17117L11200001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.01 | 17-MC-DCS-004 | TS-O-01 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001A Sodium Phosphate Injection Pump | 17L112P001A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:2/ O1011205:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL112 | 17XYSPM01AL112 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17117L11200001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.03 | 17-MC-DCS-004 | TS-O-01 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001A Sodium Phosphate Injection Pump | 17L112P001A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:4/ O1011205:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL113 | 17XSM01AL113 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17117L11300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.10 | 17-MC-DCS-004 | TS-O-05 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001A Oxygen Scavenger Injection Pump | 113P001A НАСОС ВПРЫСКА ПОГЛОТ О2 | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:19/ O1011106:10A | TS-O-05:20/ O1011106:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL113 | 17XSAM01AL113 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17117L11300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.11 | 17-MC-DCS-004 | TS-O-05 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001A Oxygen Scavenger Injection Pump | 17113P001A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:21/ O1011106:11A | TS-O-05:22/ O1011106:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL113 | 17XSRM01AL113 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17117L11300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.01 | 17-MC-DCS-004 | TS-R-05 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001A Oxygen Scavenger Injection Pump | 17113P001A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:1/ O1011108:26A | TS-R-05:2/ O1011108:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL113 | 17XYSTM01AL113 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17117L11300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.13 | 17-MC-DCS-004 | TS-O-01 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001A Oxygen Scavenger Injection Pump | 17113P001A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:14/ O1011205:7A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL113 | 17XYSPM01AL113 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17117L11300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.15 | 17-MC-DCS-004 | TS-O-01 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001A Oxygen Scavenger Injection Pump | 17113P001A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:16/ O1011205:8A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL114 | 17XSM01AL114 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17117L11400001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.16 | 17-MC-DCS-004 | TS-O-05 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001A Amine Injection Pump | 114P001A НАСОС ВПРЫСКА АМИНА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:31/ O1011106:16A | TS-O-05:32/ O1011106:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL114 | 17XSAM01AL114 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17117L11400001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.17 | 17-MC-DCS-004 | TS-O-05 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001A Amine Injection Pump | 17114P001A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:33/ O1011106:17A | TS-O-05:34/ O1011106:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL114 | 17XSRM01AL114 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17117L11400001 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.04 | 17-MC-DCS-004 | TS-R-05 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001A Amine Injection Pump | 17114P001A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:7/ O1011108:29A | TS-R-05:8/ O1011108:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL114 | 17XYSTM01AL114 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17117L11400001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.25 | 17-MC-DCS-004 | TS-O-01 | 25 | 26 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001A Amine Injection Pump | 17114P001A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:26/ O1011205:13A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01AL114 | 17XYSPM01AL114 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17117L11400001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.27 | 17-MC-DCS-004 | TS-O-01 | 27 | 28 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001A Amine Injection Pump | 17114P001A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:28/ O1011205:14A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL112 | 17XSM01BL112 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17117L11200001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.04 | 17-MC-DCS-004 | TS-O-05 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001B Sodium Phosphate Injection Pump | 112P001B НАСОС ПОДАЧИ ФОСФАТОВ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:7/ O1011106:4A | TS-O-05:8/ O1011106:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL112 | 17XSAM01BL112 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17117L11200001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.05 | 17-MC-DCS-004 | TS-O-05 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001B Sodium Phosphate Injection Pump | 17L112P001B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:9/ O1011106:5A | TS-O-05:10/ O1011106:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL112 | 17XSRM01BL112 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17117L11200001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.06 | 17-MC-DCS-004 | TS-O-05 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001B Sodium Phosphate Injection Pump | 17L112P001B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:11/ O1011106:6A | TS-O-05:12/ O1011106:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL112 | 17XYSTM01BL112 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17117L11200001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.05 | 17-MC-DCS-004 | TS-O-01 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001B Sodium Phosphate Injection Pump | 17L112P001B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:6/ O1011205:3A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL112 | 17XYSPM01BL112 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17117L11200001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.07 | 17-MC-DCS-004 | TS-O-01 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-P-001B Sodium Phosphate Injection Pump | 17L112P001B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:8/ O1011205:4A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL113 | 17XSM01BL113 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17117L11300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.12 | 17-MC-DCS-004 | TS-O-05 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001B Oxygen Scavenger Injection Pump | 113P001B НАСОС ВПРЫСКА ПОГЛОТ О2 | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:23/ O1011106:12A | TS-O-05:24/ O1011106:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL113 | 17XSAM01BL113 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17117L11300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.13 | 17-MC-DCS-004 | TS-O-05 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001B Oxygen Scavenger Injection Pump | 17113P001B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:25/ O1011106:13A | TS-O-05:26/ O1011106:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL113 | 17XSRM01BL113 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17117L11300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.02 | 17-MC-DCS-004 | TS-R-05 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001B Oxygen Scavenger Injection Pump | 17113P001B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:3/ O1011108:27A | TS-R-05:4/ O1011108:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL113 | 17XYSTM01BL113 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17117L11300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.17 | 17-MC-DCS-004 | TS-O-01 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001B Oxygen Scavenger Injection Pump | 17113P001B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:18/ O1011205:9A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL113 | 17XYSPM01BL113 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17117L11300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.19 | 17-MC-DCS-004 | TS-O-01 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-113-P-001B Oxygen Scavenger Injection Pump | 17113P001B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:20/ O1011205:10A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL114 | 17XSM01BL114 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17117L11400001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.18 | 17-MC-DCS-004 | TS-O-05 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001B Amine Injection Pump | 114P001B НАСОС ВПРЫСКА АМИНА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:35/ O1011106:18A | TS-O-05:36/ O1011106:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL114 | 17XSAM01BL114 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17117L11400001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.19 | 17-MC-DCS-004 | TS-O-05 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001B Amine Injection Pump | 17114P001B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:37/ O1011106:19A | TS-O-05:38/ O1011106:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL114 | 17XSRM01BL114 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17117L11400001 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.05 | 17-MC-DCS-004 | TS-R-05 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001B Amine Injection Pump | 17114P001B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:9/ O1011108:30A | TS-R-05:10/ O1011108:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL114 | 17XYSTM01BL114 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17117L11400001 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.01 | 17-MC-DCS-004 | TS-O-02 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001B Amine Injection Pump | 17114P001B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:2/ O1011205:15A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01BL114 | 17XYSPM01BL114 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17117L11400001 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.03 | 17-MC-DCS-004 | TS-O-02 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-114-P-001B Amine Injection Pump | 17114P001B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:4/ O1011205:16A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L112 | 17XSM01L112 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17117L11200001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.07 | 17-MC-DCS-004 | TS-O-05 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-AGM-001 Sodium Phosphate tank agitator | 17L112AGM001 СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:13/ O1011106:7A | TS-O-05:14/ O1011106:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L112 | 17XSAM01L112 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17117L11200001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.08 | 17-MC-DCS-004 | TS-O-05 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-AGM-001 Sodium Phosphate tank agitator | 17L112AGM001 ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:15/ O1011106:8A | TS-O-05:16/ O1011106:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L112 | 17XSRM01L112 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17117L11200001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.09 | 17-MC-DCS-004 | TS-O-05 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-AGM-001 Sodium Phosphate tank agitator | 17L112AGM001 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:17/ O1011106:9A | TS-O-05:18/ O1011106:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L112 | 17XYSTM01L112 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17117L11200001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.09 | 17-MC-DCS-004 | TS-O-01 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-AGM-001 Sodium Phosphate tank agitator | МЕШАЛКА БАКА ФОСФАТА НАТРИЯ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:10/ O1011205:5A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L112 | 17XYSPM01L112 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17117L11200001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.11 | 17-MC-DCS-004 | TS-O-01 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-112-AGM-001 Sodium Phosphate tank agitator | 17L112AGM001 ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:12/ O1011205:6A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L113 | 17XSM01L113 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17117L11300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.14 | 17-MC-DCS-004 | TS-O-05 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-113-AGM-001 Oxygen Scavenger tank agitator | 113AGM001 МЕШАЛКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:27/ O1011106:14A | TS-O-05:28/ O1011106:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L113 | 17XSAM01L113 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17117L11300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.15 | 17-MC-DCS-004 | TS-O-05 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-113-AGM-001 Oxygen Scavenger tank agitator | 17L113AGM001 ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:29/ O1011106:15A | TS-O-05:30/ O1011106:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L113 | 17XSRM01L113 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17117L11300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.03 | 17-MC-DCS-004 | TS-R-05 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-113-AGM-001 Oxygen Scavenger tank agitator | 17L113AGM001 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:5/ O1011108:28A | TS-R-05:6/ O1011108:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L113 | 17XYSTM01L113 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17117L11300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.21 | 17-MC-DCS-004 | TS-O-01 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-113-AGM-001 Sodium Phosphate tank agitator | 17L113AGM001 ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:22/ O1011205:11A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L113 | 17XYSPM01L113 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17117L11300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-012BL02 | 30 Core | C.23 | 17-MC-DCS-004 | TS-O-01 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-113-AGM-001 Sodium Phosphate tank agitator | 17L113AGM001 СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-01:24/ O1011205:12A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L114 | 17XSM01L114 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17117L11400001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.20 | 17-MC-DCS-004 | TS-O-05 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-114-AG-001 Amine tank agitator | 114AG001 МЕШАЛКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:39/ O1011106:20A | TS-O-05:40/ O1011106:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L114 | 17XSAM01L114 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17117L11400001 | DCS_DI_03 | MCC |  | 17-I-DD-N-008BL02 | 24 Pair | Pr.21 | 17-MC-DCS-004 | TS-O-05 | 41 | 42 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-114-AG-001 Amine tank agitator | 17L114AG001 ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:41/ O1011106:21A | TS-O-05:42/ O1011106:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L114 | 17XSRM01L114 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remotee status | 4124-FY-VD-BD17117L11400001 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.06 | 17-MC-DCS-004 | TS-R-05 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-114-AG-001 Amine tank agitator | 17L114AG001 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:11/ O1011108:31A | TS-R-05:12/ O1011108:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L114 | 17XYSTM01L114 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17117L11300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.05 | 17-MC-DCS-004 | TS-O-02 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-114-AG-001 Amine tank agitator | 17L114AG001 ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:6/ O1011205:17A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -01L114 | 17XYSPM01L114 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17117L11300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.07 | 17-MC-DCS-004 | TS-O-02 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-114-AG-001 Amine tank agitator | 17L114AG001 СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:8/ O1011205:18A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -A | 17XSM020A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P020050 | DCS_DI_03 | MCC |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.01 | 17-MC-DCS-003 | TS-H-01 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020A | P020A НАСОС ПАРОВОГО КОНДЕНСАТА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:1/ O1010208:8A | TS-H-01:2/ O1010208:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -A | 17XSAM020A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P020050 | DCS_DI_03 | MCC |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.02 | 17-MC-DCS-003 | TS-H-01 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020A | 17-P-020A ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:3/ O1010208:9A | TS-H-01:4/ O1010208:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -A | 17XSRM020A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P020050 | DCS_DI_03 | MCC |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.03 | 17-MC-DCS-003 | TS-H-01 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020A | 17-P-020A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:5/ O1010208:10A | TS-H-01:6/ O1010208:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -A | 17XYSPM020A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P020050 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.17 | 17-MC-DCS-003 | TS-G-07 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020A | 17-P-020A СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:18/ O1010214:13A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -A | 17XYSTM020A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P020050 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.19 | 17-MC-DCS-003 | TS-G-07 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020A | 17-P-020A ПУСК | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:20/ O1010214:14A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -B | 17XSAM020B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P020050 | DCS_DI_03 | MCC |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.04 | 17-MC-DCS-003 | TS-H-01 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020B | 17-P-020B ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:7/ O1010208:11A | TS-H-01:8/ O1010208:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -B | 17XSRM020B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P020050 | DCS_DI_03 | MCC |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.05 | 17-MC-DCS-003 | TS-H-01 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020B | 17-P-020B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:9/ O1010208:12A | TS-H-01:10/ O1010208:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -B | 17XYSPM020B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P020050 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.21 | 17-MC-DCS-003 | TS-G-07 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020B | 17-P-020B СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:22/ O1010214:15A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -B | 17XYSTM020B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P020050 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.23 | 17-MC-DCS-003 | TS-G-07 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020B | 17-P-020B ПУСК | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:24/ O1010214:16A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -020 -B | 17XSM020B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P020050 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.13 | 17-MC-DCS-005 | TS-G-04 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | LP Condensate 17-P-020B | P020B НАСОС ПАРОВОГО КОНДЕНСАТА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:25/ O1010300:6A | TS-G-04:26/ O1010300:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -021 | 17XSM021 | 17-ID-0201 | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P021069 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.07 | 17-MC-DCS-003 | TS-F-05 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric Motor 17-P-021 | P021 НАСОС НЕКОНД. ТЕХНОЛ. КОНД. | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:13/ O1010207:31A | TS-F-05:14/ O1010207:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -021 | 17XSAM021 | 17-ID-0201 | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P021069 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.08 | 17-MC-DCS-003 | TS-F-05 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric Motor 17-P-021 | 17-P-021 ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:15/ O1010207:32A | TS-F-05:16/ O1010207:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -021 | 17XSRM021 | 17-ID-0201 | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-GG-VD-BD17217P021069 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.09 | 17-MC-DCS-003 | TS-F-05 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric Motor 17-P-021 | 17-P-021 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:17/ O1010208:1A | TS-F-05:18/ O1010208:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -021 | 17XYSPM021 | 17-ID-0201 | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P021069 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.13 | 17-MC-DCS-003 | TS-G-05 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric Motor 17-P-021 | 17-P-021 СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:14/ O1010213:25A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -021 | 17XYSTM021 | 17-ID-0201 | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P021069 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.15 | 17-MC-DCS-003 | TS-G-05 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric Motor 17-P-021 | 17-P-021 ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:16/ O1010213:26A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -A | 17XSM030A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P030086 | DCS_DI_03 | MCC |  | 17-I-DD-N-006BL02 | 24 Pair | Pr.01 | 17-MC-DCS-005 | TS-F-01 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030A | P030A НАСОС КОНДЕНСАТА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-01:1/ O1010115:1A | TS-F-01:2/ O1010115:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -A | 17XSAM030A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P030086 | DCS_DI_03 | MCC |  | 17-I-DD-N-006BL02 | 24 Pair | Pr.02 | 17-MC-DCS-005 | TS-F-01 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030A | 17-P-030A ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-01:3/ O1010115:2A | TS-F-01:4/ O1010115:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -A | 17XSRM030A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P030086 | DCS_DI_03 | MCC |  | 17-I-DD-N-006BL02 | 24 Pair | Pr.03 | 17-MC-DCS-005 | TS-F-01 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030A | 17-P-030A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-01:5/ O1010115:3A | TS-F-01:6/ O1010115:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -A | 17XYSPM030A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P030086 | DCS_DO_03 | MCC |  | 17-I-CD-N-019BL02 | 30 Core | C.05 | 17-MC-DCS-005 | TS-H-04 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030A | 17-P-030A СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-04:6/ O1010215:3A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -A | 17XYSTM030A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P030086 | DCS_DO_03 | MCC |  | 17-I-CD-N-019BL02 | 30 Core | C.07 | 17-MC-DCS-005 | TS-H-04 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030A | 17-P-030A ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-04:8/ O1010215:4A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -B | 17XSM030B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P030086 | DCS_DI_03 | MCC |  | 17-I-DD-N-006BL02 | 24 Pair | Pr.04 | 17-MC-DCS-005 | TS-F-01 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030B | P030B НАСОС КОНДЕНСАТА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-01:7/ O1010115:4A | TS-F-01:8/ O1010115:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -B | 17XSAM030B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P030086 | DCS_DI_03 | MCC |  | 17-I-DD-N-006BL02 | 24 Pair | Pr.05 | 17-MC-DCS-005 | TS-F-01 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030B | 17-P-030B ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-01:9/ O1010115:5A | TS-F-01:10/ O1010115:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -B | 17XSRM030B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P030086 | DCS_DI_03 | MCC |  | 17-I-DD-N-006BL02 | 24 Pair | Pr.06 | 17-MC-DCS-005 | TS-F-01 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030B | 17-P-030B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-01:11/ O1010115:6A | TS-F-01:12/ O1010115:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -B | 17XYSPM030B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P030086 | DCS_DO_03 | MCC |  | 17-I-CD-N-019BL02 | 30 Core | C.09 | 17-MC-DCS-005 | TS-H-04 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030B | 17-P-030B СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-04:10/ O1010215:5A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -B | 17XYSTM030B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P030086 | DCS_DO_03 | MCC |  | 17-I-CD-N-019BL02 | 30 Core | C.11 | 17-MC-DCS-005 | TS-H-04 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030B | 17-P-030B ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-04:12/ O1010215:6A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -C | 17XSM030C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21703004 | DCS_DI_03 | MCC |  | 17-I-DD-N-006BL02 | 24 Pair | Pr.07 | 17-MC-DCS-005 | TS-F-01 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030C | P030C НАСОС КОНДЕНСАТА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-01:13/ O1010115:7A | TS-F-01:14/ O1010115:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -C | 17XSAM030C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21703004 | DCS_DI_03 | MCC |  | 17-I-DD-N-006BL02 | 24 Pair | Pr.08 | 17-MC-DCS-005 | TS-F-01 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030C | 17-P-030C ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-01:15/ O1010115:8A | TS-F-01:16/ O1010115:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -C | 17XSRM030C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21703004 | DCS_DI_03 | MCC |  | 17-I-DD-N-006BL02 | 24 Pair | Pr.09 | 17-MC-DCS-005 | TS-F-01 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030C | 17-P-030C МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-01:17/ O1010115:9A | TS-F-01:18/ O1010115:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -C | 17XYSPM030C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21703004 | DCS_DO_03 | MCC |  | 17-I-CD-N-019BL02 | 30 Core | C.13 | 17-MC-DCS-005 | TS-H-04 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030C | 17-P-030C СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-04:14/ O1010215:7A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -030 -C | 17XYSTM030C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21703004 | DCS_DO_03 | MCC |  | 17-I-CD-N-019BL02 | 30 Core | C.15 | 17-MC-DCS-005 | TS-H-04 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Filter Feed Pump 17-P-030C | 17-P-030C ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-04:16/ O1010215:8A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -A | 17XSM031A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P031102 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.13 | 17-MC-DCS-003 | TS-F-05 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031A | P031A НАСОС КОНДЕНСАТА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:25/ O1010208:5A | TS-F-05:26/ O1010208:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -A | 17XSAM031A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P031102 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.14 | 17-MC-DCS-003 | TS-F-05 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031A | 17-P-031A ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:27/ O1010208:6A | TS-F-05:28/ O1010208:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -A | 17XSRM031A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P031102 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.15 | 17-MC-DCS-003 | TS-F-05 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031A | 17-P-031A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:29/ O1010208:7A | TS-F-05:30/ O1010208:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -A | 17XYSPM031A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P031102 | DCS_DO_03 | MCC |  | 17-I-CD-N-010BL02 | 30 Core | C.01 | 17-MC-DCS-003 | TS-G-06 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031A | 17-P-031A СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-06:2/ O1010213:31A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -A | 17XYSTM031A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P031102 | DCS_DO_03 | MCC |  | 17-I-CD-N-010BL02 | 30 Core | C.03 | 17-MC-DCS-003 | TS-G-06 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031A | P030B НАСОС КОНДЕНСАТА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-06:4/ O1010213:32A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -B | 17XSM031B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P031102 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.10 | 17-MC-DCS-005 | TS-F-04 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031B | P031B НАСОС КОНДЕНСАТА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:19/ O1010115:20A | TS-F-04:20/ O1010115:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -B | 17XSAM031B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P031102 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.11 | 17-MC-DCS-005 | TS-F-04 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031B | 17-P-031B ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:21/ O1010115:21A | TS-F-04:22/ O1010115:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -B | 17XSRM031B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P031102 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.12 | 17-MC-DCS-005 | TS-F-04 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031B | 17-P-031B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:23/ O1010115:22A | TS-F-04:24/ O1010115:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -B | 17XYSPM031B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P031102 | DCS_DO_03 | MCC |  | 17-I-CD-N-010BL02 | 30 Core | C.05 | 17-MC-DCS-003 | TS-G-06 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031B | 17-P-031B СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-06:6/ O1010214:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -B | 17XYSTM031B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P031102 | DCS_DO_03 | MCC |  | 17-I-CD-N-010BL02 | 30 Core | C.07 | 17-MC-DCS-003 | TS-G-06 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031B | P030B НАСОС КОНДЕНСАТА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-06:8/ O1010214:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -C | 17XSM031C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21703003 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.13 | 17-MC-DCS-005 | TS-F-04 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031C | P031C НАСОС КОНДЕНСАТА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:25/ O1010115:23A | TS-F-04:26/ O1010115:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -C | 17XSAM031C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21703003 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.14 | 17-MC-DCS-005 | TS-F-04 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031C | 17-P-031C ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:27/ O1010115:24A | TS-F-04:28/ O1010115:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -C | 17XSRM031C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21703003 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.15 | 17-MC-DCS-005 | TS-F-04 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031C | 17-P-031C МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:29/ O1010115:25A | TS-F-04:30/ O1010115:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -C | 17XYSPM031C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21703003 | DCS_DO_03 | MCC |  | 17-I-CD-N-010BL02 | 30 Core | C.09 | 17-MC-DCS-003 | TS-G-06 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031C | 17-P-031C СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-06:10/ O1010214:3A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -031 -C | 17XYSTM031C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21703003 | DCS_DO_03 | MCC |  | 17-I-CD-N-010BL02 | 30 Core | C.11 | 17-MC-DCS-003 | TS-G-06 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Filter Feed Pump 17-P-031C | 17-P-031C ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-06:12/ O1010214:4A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -A | 17XSM032A | 17-ID-0301_shA | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P032118 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.10 | 17-MC-DCS-003 | TS-F-05 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032A | P032A НАСОС ДЕМ. ВОДЫ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:19/ O1010208:2A | TS-F-05:20/ O1010208:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -A | 17XSAM032A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P032118 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.11 | 17-MC-DCS-003 | TS-F-05 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032A | 17-P-032A ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:21/ O1010208:3A | TS-F-05:22/ O1010208:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -A | 17XSRM032A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P032118 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.12 | 17-MC-DCS-003 | TS-F-05 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032A | 17-P-032A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:23/ O1010208:4A | TS-F-05:24/ O1010208:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -A | 17XYSPM032A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P032118 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.17 | 17-MC-DCS-003 | TS-G-05 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032A | 17-P-032A СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:18/ O1010213:27A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -A | 17XYSTM032A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P032118 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.19 | 17-MC-DCS-003 | TS-G-05 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032A | 17-P-032A ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:20/ O1010213:28A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -B | 17XSM032B | 17-ID-0301_shA | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P032118 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.04 | 17-MC-DCS-005 | TS-F-04 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032B | P032A НАСОС ДЕМ. ВОДЫ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:7/ O1010115:14A | TS-F-04:8/ O1010115:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -B | 17XSAM032B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P032118 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.05 | 17-MC-DCS-005 | TS-F-04 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032B | 17-P-032B ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:9/ O1010115:15A | TS-F-04:10/ O1010115:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -B | 17XSRM032B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P032118 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.06 | 17-MC-DCS-005 | TS-F-04 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032B | 17-P-032B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:11/ O1010115:16A | TS-F-04:12/ O1010115:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -B | 17XYSPM032B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P032118 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.21 | 17-MC-DCS-003 | TS-G-05 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032B | 17-P-032B СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:22/ O1010213:29A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -B | 17XYSTM032B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P032118 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.23 | 17-MC-DCS-003 | TS-G-05 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032B | 17-P-032B ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:24/ O1010213:30A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -C | 17XSM032C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21703001 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.07 | 17-MC-DCS-005 | TS-F-04 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032C | P032C НАСОС ДЕМ. ВОДЫ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:13/ O1010115:17A | TS-F-04:14/ O1010115:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -C | 17XSAM032C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21703001 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.08 | 17-MC-DCS-005 | TS-F-04 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032C | 17-P-032C ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:15/ O1010115:18A | TS-F-04:16/ O1010115:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -C | 17XSRM032C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21703001 | DCS_DI_03 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.09 | 17-MC-DCS-005 | TS-F-04 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032C | 17-P-032C МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:17/ O1010115:19A | TS-F-04:18/ O1010115:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -C | 17XYSPM032C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21703001 | DCS_DO_03 | MCC |  | 17-I-CD-N-019BL02 | 30 Core | C.01 | 17-MC-DCS-005 | TS-H-04 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032C | 17-P-032C СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-04:2/ O1010215:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -032 -C | 17XYSTM032C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21703001 | DCS_DO_03 | MCC |  | 17-I-CD-N-019BL02 | 30 Core | C.03 | 17-MC-DCS-005 | TS-H-04 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Demi Water Pump 17-P-032C | 17-P-032C ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-H-04:4/ O1010215:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07034 | 17MXSA07034 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.01 | 17-MC-DCS-001 | TS-F-02 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CWS to Pump Basin | 17-MOV-07034 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:1/ O1010200:5A | TS-F-02:2/ O1010200:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07034 | 17MXSR07034 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.02 | 17-MC-DCS-001 | TS-F-02 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CWS to Pump Basin | 17-MOV-07034 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:3/ O1010200:6A | TS-F-02:4/ O1010200:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07034 | 17MZSH07034 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.03 | 17-MC-DCS-001 | TS-F-02 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CWS to Pump Basin | 17-MOV-07034 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:5/ O1010200:7A | TS-F-02:6/ O1010200:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07034 | 17MZSL07034 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.04 | 17-MC-DCS-001 | TS-F-02 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CWS to Pump Basin | 17-MOV-07034 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:7/ O1010200:8A | TS-F-02:8/ O1010200:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07034 | 17MXYSP07034 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.01 | 17-MC-DCS-001 | TS-G-01 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 1 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | CWS to Pump Basin | 17-MOV-07034 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:1/ O1010210:1A | TS-G-01:2/ O1010210:1C | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07034 | 17MXYH07034 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.03 | 17-MC-DCS-001 | TS-G-01 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 2 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | CWS to Pump Basin | 17-MOV-07034 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:3/ O1010210:2A | TS-G-01:4/ O1010210:2C | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07034 | 17MXYL07034 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.05 | 17-MC-DCS-001 | TS-G-01 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 3 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | CWS to Pump Basin | 17-MOV-07034 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:5/ O1010210:3A | TS-G-01:6/ O1010210:3C | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07035 | 17MXSA07035 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.05 | 17-MC-DCS-001 | TS-F-02 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071A Discharge line | 17-MOV-07035 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:9/ O1010200:9A | TS-F-02:10/ O1010200:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07035 | 17MXSR07035 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.06 | 17-MC-DCS-001 | TS-F-02 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071A Discharge line | 17-MOV-07035 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:11/ O1010200:10A | TS-F-02:12/ O1010200:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07035 | 17MZSH07035 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.07 | 17-MC-DCS-001 | TS-F-02 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071A Discharge line | 17-MOV-07035 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:13/ O1010200:11A | TS-F-02:14/ O1010200:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07035 | 17MZSL07035 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.08 | 17-MC-DCS-001 | TS-F-02 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071A Discharge line | 17-MOV-07035 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:15/ O1010200:12A | TS-F-02:16/ O1010200:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07035 | 17MXYSP07035 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.07 | 17-MC-DCS-001 | TS-G-01 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 4 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071A Discharge line | 17-MOV-07035 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:7/ O1010210:4A | TS-G-01:8/ O1010210:4C | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07035 | 17MXYH07035 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.09 | 17-MC-DCS-001 | TS-G-01 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 5 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071A Discharge line | 17-MOV-07035 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:9/ O1010210:5A | TS-G-01:10/ O1010210:5C | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07035 | 17MXYL07035 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.11 | 17-MC-DCS-001 | TS-G-01 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 6 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071A Discharge line | 17-MOV-07035 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:11/ O1010210:6A | TS-G-01:12/ O1010210:6C | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07036 | 17MXSA07036 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.09 | 17-MC-DCS-001 | TS-F-02 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071B Discharge line | 17-MOV-07036 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:17/ O1010200:13A | TS-F-02:18/ O1010200:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07036 | 17MXSR07036 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.10 | 17-MC-DCS-001 | TS-F-02 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071B Discharge line | 17-MOV-07036 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:19/ O1010200:14A | TS-F-02:20/ O1010200:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07036 | 17MZSH07036 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.11 | 17-MC-DCS-001 | TS-F-02 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071B Discharge line | 17-MOV-07036 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:21/ O1010200:15A | TS-F-02:22/ O1010200:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07036 | 17MZSL07036 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.12 | 17-MC-DCS-001 | TS-F-02 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071B Discharge line | 17-MOV-07036 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:23/ O1010200:16A | TS-F-02:24/ O1010200:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07036 | 17MXYSP07036 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.13 | 17-MC-DCS-001 | TS-G-01 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 7 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071B Discharge line | 17-MOV-07036 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:13/ O1010210:7A | TS-G-01:14/ O1010210:7C | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07036 | 17MXYH07036 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.15 | 17-MC-DCS-001 | TS-G-01 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 8 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071B Discharge line | 17-MOV-07036 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:15/ O1010210:8A | TS-G-01:16/ O1010210:8C | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07036 | 17MXYL07036 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.17 | 17-MC-DCS-001 | TS-G-01 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 9 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071B Discharge line | 17-MOV-07036 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:17/ O1010210:9A | TS-G-01:18/ O1010210:9C | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07037 | 17MXSA07037 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.13 | 17-MC-DCS-001 | TS-F-02 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071C Discharge line | 17-MOV-07037 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:25/ O1010200:17A | TS-F-02:26/ O1010200:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07037 | 17MXSR07037 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.14 | 17-MC-DCS-001 | TS-F-02 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071C Discharge line | 17-MOV-07037 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:27/ O1010200:18A | TS-F-02:28/ O1010200:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07037 | 17MZSH07037 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.15 | 17-MC-DCS-001 | TS-F-02 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071C Discharge line | 17-MOV-07037 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:29/ O1010200:19A | TS-F-02:30/ O1010200:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07037 | 17MZSL07037 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.16 | 17-MC-DCS-001 | TS-F-02 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071C Discharge line | 17-MOV-07037 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-02:31/ O1010200:20A | TS-F-02:32/ O1010200:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07037 | 17MXYSP07037 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.19 | 17-MC-DCS-001 | TS-G-01 | 19 | 20 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 10 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071C Discharge line | 17-MOV-07037 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:19/ O1010210:10A | TS-G-01:20/ O1010210:10C | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07037 | 17MXYH07037 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.21 | 17-MC-DCS-001 | TS-G-01 | 21 | 22 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 11 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071C Discharge line | 17-MOV-07037 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:21/ O1010210:11A | TS-G-01:22/ O1010210:11C | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07037 | 17MXYL07037 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL07 | 30 Core | C.23 | 17-MC-DCS-001 | TS-G-01 | 23 | 24 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 12 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071C Discharge line | 17-MOV-07037 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-01:23/ O1010210:12A | TS-G-01:24/ O1010210:12C | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07038 | 17MXSA07038 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.01 | 17-MC-DCS-001 | TS-F-05 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071D Discharge line | 17-MOV-07038 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:1/ O1010201:1A | TS-F-05:2/ O1010201:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07038 | 17MXSR07038 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.02 | 17-MC-DCS-001 | TS-F-05 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071D Discharge line | 17-MOV-07038 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:3/ O1010201:2A | TS-F-05:4/ O1010201:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07038 | 17MZSH07038 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.03 | 17-MC-DCS-001 | TS-F-05 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071D Discharge line | 17-MOV-07038 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:5/ O1010201:3A | TS-F-05:6/ O1010201:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07038 | 17MZSL07038 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707003 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.04 | 17-MC-DCS-001 | TS-F-05 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071D Discharge line | 17-MOV-07038 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:7/ O1010201:4A | TS-F-05:8/ O1010201:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07038 | 17MXYSP07038 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.01 | 17-MC-DCS-001 | TS-G-03 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 15 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071D Discharge line | 17-MOV-07038 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:1/ O1010210:15A | TS-G-03:2/ O1010210:15C | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07038 | 17MXYH07038 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.03 | 17-MC-DCS-001 | TS-G-03 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 16 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071D Discharge line | 17-MOV-07038 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:3/ O1010210:16A | TS-G-03:4/ O1010210:16C | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07038 | 17MXYL07038 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707003 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.05 | 17-MC-DCS-001 | TS-G-03 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 17 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071D Discharge line | 17-MOV-07038 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:5/ O1010210:17A | TS-G-03:6/ O1010210:17C | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07039 | 17MXSA07039 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.05 | 17-MC-DCS-001 | TS-F-05 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071E Discharge line | 17-MOV-07039 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:9/ O1010201:5A | TS-F-05:10/ O1010201:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07039 | 17MXSR07039 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.06 | 17-MC-DCS-001 | TS-F-05 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071E Discharge line | 17-MOV-07039 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:11/ O1010201:6A | TS-F-05:12/ O1010201:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07039 | 17MZSH07039 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.07 | 17-MC-DCS-001 | TS-F-05 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071E Discharge line | 17-MOV-07039 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:13/ O1010201:7A | TS-F-05:14/ O1010201:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07039 | 17MZSL07039 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.08 | 17-MC-DCS-001 | TS-F-05 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071E Discharge line | 17-MOV-07039 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:15/ O1010201:8A | TS-F-05:16/ O1010201:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07039 | 17MXYSP07039 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.07 | 17-MC-DCS-001 | TS-G-03 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 18 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071E Discharge line | 17-MOV-07039 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:7/ O1010210:18A | TS-G-03:8/ O1010210:18C | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07039 | 17MXYH07039 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.09 | 17-MC-DCS-001 | TS-G-03 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 19 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071E Discharge line | 17-MOV-07039 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:9/ O1010210:19A | TS-G-03:10/ O1010210:19C | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07039 | 17MXYL07039 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.11 | 17-MC-DCS-001 | TS-G-03 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 20 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071E Discharge line | 17-MOV-07039 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:11/ O1010210:20A | TS-G-03:12/ O1010210:20C | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07040 | 17MXSA07040 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.09 | 17-MC-DCS-001 | TS-F-05 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071F Discharge line | 17-MOV-07040 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:17/ O1010201:9A | TS-F-05:18/ O1010201:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07040 | 17MXSR07040 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.10 | 17-MC-DCS-001 | TS-F-05 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071F Discharge line | 17-MOV-07040 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:19/ O1010201:10A | TS-F-05:20/ O1010201:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07040 | 17MZSH07040 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.11 | 17-MC-DCS-001 | TS-F-05 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071F Discharge line | 17-MOV-07040 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:21/ O1010201:11A | TS-F-05:22/ O1010201:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07040 | 17MZSL07040 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.12 | 17-MC-DCS-001 | TS-F-05 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071F Discharge line | 17-MOV-07040 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:23/ O1010201:12A | TS-F-05:24/ O1010201:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07040 | 17MXYSP07040 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.13 | 17-MC-DCS-001 | TS-G-03 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 21 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071F Discharge line | 17-MOV-07040 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:13/ O1010210:21A | TS-G-03:14/ O1010210:21C | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07040 | 17MXYH07040 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.15 | 17-MC-DCS-001 | TS-G-03 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 22 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071F Discharge line | 17-MOV-07040 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:15/ O1010210:22A | TS-G-03:16/ O1010210:22C | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07040 | 17MXYL07040 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.17 | 17-MC-DCS-001 | TS-G-03 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 23 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071F Discharge line | 17-MOV-07040 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:17/ O1010210:23A | TS-G-03:18/ O1010210:23C | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07041 | 17MXSA07041 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.13 | 17-MC-DCS-001 | TS-F-05 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071G Discharge line | 17-MOV-07041 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:25/ O1010201:13A | TS-F-05:26/ O1010201:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07041 | 17MXSR07041 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.14 | 17-MC-DCS-001 | TS-F-05 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071G Discharge line | 17-MOV-07041 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:27/ O1010201:14A | TS-F-05:28/ O1010201:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07041 | 17MZSH07041 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.15 | 17-MC-DCS-001 | TS-F-05 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071G Discharge line | 17-MOV-07041 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:29/ O1010201:15A | TS-F-05:30/ O1010201:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07041 | 17MZSL07041 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL07 | 24 Pair | Pr.16 | 17-MC-DCS-001 | TS-F-05 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071G Discharge line | 17-MOV-07041 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-05:31/ O1010201:16A | TS-F-05:32/ O1010201:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07041 | 17MXYSP07041 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.01 | 17-MC-DCS-001 | TS-G-05 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 7 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071G Discharge line | 17-MOV-07041 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-05:1/ O1010211:7A | TS-G-05:2/ O1010211:7C | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07041 | 17MXYH07041 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.03 | 17-MC-DCS-001 | TS-G-05 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 8 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071G Discharge line | 17-MOV-07041 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-05:3/ O1010211:8A | TS-G-05:4/ O1010211:8C | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07041 | 17MXYL07041 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.05 | 17-MC-DCS-001 | TS-G-05 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 9 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-071G Discharge line | 17-MOV-07041 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-05:5/ O1010211:9A | TS-G-05:6/ O1010211:9C | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07042 | 17MXSA07042 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.01 | 17-MC-DCS-002 | TS-R-03 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-073A Discharge line | 17-MOV-07042 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-R-03:1/ O1010204:1A | TS-R-03:2/ O1010204:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07042 | 17MXSR07042 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.02 | 17-MC-DCS-002 | TS-R-03 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-073A Discharge line | 17-MOV-07042 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-R-03:3/ O1010204:2A | TS-R-03:4/ O1010204:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07042 | 17MZSH07042 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.03 | 17-MC-DCS-002 | TS-R-03 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-073A Discharge line | 17-MOV-07042 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-R-03:5/ O1010204:3A | TS-R-03:6/ O1010204:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07042 | 17MZSL07042 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.04 | 17-MC-DCS-002 | TS-R-03 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-073A Discharge line | 17-MOV-07042 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-R-03:7/ O1010204:4A | TS-R-03:8/ O1010204:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07042 | 17MXYSP07042 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.19 | 17-MC-DCS-001 | TS-G-03 | 19 | 20 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 24 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-073A Discharge line | 17-MOV-07042 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:19/ O1010210:24A | TS-G-03:20/ O1010210:24C | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07042 | 17MXYH07042 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.21 | 17-MC-DCS-001 | TS-G-03 | 21 | 22 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 25 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-073A Discharge line | 17-MOV-07042 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:21/ O1010210:25A | TS-G-03:22/ O1010210:25C | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07042 | 17MXYL07042 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL07 | 30 Core | C.23 | 17-MC-DCS-001 | TS-G-03 | 23 | 24 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 26 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-073A Discharge line | 17-MOV-07042 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-03:23/ O1010210:26A | TS-G-03:24/ O1010210:26C | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07043 | 17MXSA07043 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.05 | 17-MC-DCS-002 | TS-R-03 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-073B Discharge line | 17-MOV-07043 ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-R-03:9/ O1010204:5A | TS-R-03:10/ O1010204:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07043 | 17MXSR07043 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.06 | 17-MC-DCS-002 | TS-R-03 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-073B Discharge line | 17-MOV-07043 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-R-03:11/ O1010204:6A | TS-R-03:12/ O1010204:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07043 | 17MZSH07043 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.07 | 17-MC-DCS-002 | TS-R-03 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-073B Discharge line | 17-MOV-07043 ОТКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-R-03:13/ O1010204:7A | TS-R-03:14/ O1010204:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07043 | 17MZSL07043 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-XZ-DM-21707007 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.08 | 17-MC-DCS-002 | TS-R-03 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-073B Discharge line | 17-MOV-07043 ЗАКРЫТО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-R-03:15/ O1010204:8A | TS-R-03:16/ O1010204:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07043 | 17MXYSP07043 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.07 | 17-MC-DCS-001 | TS-G-05 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 10 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-073B Discharge line | 17-MOV-07043 СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-05:7/ O1010211:10A | TS-G-05:8/ O1010211:10C | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07043 | 17MXYH07043 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.09 | 17-MC-DCS-001 | TS-G-05 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 11 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-073B Discharge line | 17-MOV-07043 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-05:9/ O1010211:11A | TS-G-05:10/ O1010211:11C | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -07043 | 17MXYL07043 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-XZ-DM-21707007 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL07 | 30 Core | C.11 | 17-MC-DCS-001 | TS-G-05 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 12 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-P-073B Discharge line | 17-MOV-07043 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-05:11/ O1010211:12A | TS-G-05:12/ O1010211:12C | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -A | 17XSM071A |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-GG-VD-BD17617P071001_SH.3 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.02 | 17-MC-DCS-003 | TS-F-03 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071A | P071A ЦИРКУЛЯЦИОННЫЙ НАСОС | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:3/ O1010206:24A | TS-F-03:4/ O1010206:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -A | 17XSAM071A |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-GG-VD-BD17617P071001_SH.3 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.03 | 17-MC-DCS-003 | TS-F-03 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071A | 17-P-071A ДОСТУПЕН | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:5/ O1010206:25A | TS-F-03:6/ O1010206:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -A | 17XSRM071A |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-GG-VD-BD17617P071001_SH.3 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.04 | 17-MC-DCS-003 | TS-F-03 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071A | 17-P-071A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:7/ O1010206:26A | TS-F-03:8/ O1010206:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -A | 17XYSPM071A |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-GG-VD-BD17617P071001_SH.3 | DCS_DO_04 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.07 | 17-MC-DCS-003 | TS-G-03 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071A | 17-P-071A СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:8/ O1010212:29A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -A | 17XYSTM071A |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-GG-VD-BD17617P071001_SH.3 | DCS_DO_04 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.09 | 17-MC-DCS-003 | TS-G-03 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071A | 17-P-071A ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:10/ O1010212:30A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -B | 17XSM071B |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-GG-VD-BD17617P071001_SH.4 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.05 | 17-MC-DCS-003 | TS-F-03 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071B | P071B ЦИРКУЛЯЦИОННЫЙ НАСОС | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:9/ O1010206:27A | TS-F-03:10/ O1010206:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -B | 17XSAM071B |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-GG-VD-BD17617P071001_SH.4 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.06 | 17-MC-DCS-003 | TS-F-03 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071B | 17-P-071B ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:11/ O1010206:28A | TS-F-03:12/ O1010206:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -B | 17XSRM071B |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-GG-VD-BD17617P071001_SH.4 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.07 | 17-MC-DCS-003 | TS-F-03 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071B | 17-P-071B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:13/ O1010206:29A | TS-F-03:14/ O1010206:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -B | 17XYSPM071B |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-GG-VD-BD17617P071001_SH.4 | DCS_DO_04 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.11 | 17-MC-DCS-003 | TS-G-03 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071B | 17-P-071B СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:12/ O1010212:31A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -B | 17XYSTM071B |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-GG-VD-BD17617P071001_SH.4 | DCS_DO_04 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.13 | 17-MC-DCS-003 | TS-G-03 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071B | 17-P-071B ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:14/ O1010212:32A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -C | 17XSM071C |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-GG-VD-BD17617P071001_SH.5 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.08 | 17-MC-DCS-003 | TS-F-03 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071C | P071C ЦИРКУЛЯЦИОННЫЙ НАСОС | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:15/ O1010206:30A | TS-F-03:16/ O1010206:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -C | 17XSAM071C |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-GG-VD-BD17617P071001_SH.5 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.09 | 17-MC-DCS-003 | TS-F-03 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071C | 17-P-071C ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:17/ O1010206:31A | TS-F-03:18/ O1010206:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -C | 17XSRM071C |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-GG-VD-BD17617P071001_SH.5 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.10 | 17-MC-DCS-003 | TS-F-03 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071C | 17-P-071C МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:19/ O1010206:32A | TS-F-03:20/ O1010206:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -C | 17XYSPM071C |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-GG-VD-BD17617P071001_SH.5 | DCS_DO_04 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.15 | 17-MC-DCS-003 | TS-G-03 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071C | 17-P-071C СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:16/ O1010213:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -C | 17XYSTM071C |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-GG-VD-BD17617P071001_SH.5 | DCS_DO_04 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.17 | 17-MC-DCS-003 | TS-G-03 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071C | 17-P-071C ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:18/ O1010213:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -D | 17XSM071D |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-GG-VD-BD17617P071001_SH.6 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.11 | 17-MC-DCS-003 | TS-F-03 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071D | P071D ЦИРКУЛЯЦИОННЫЙ НАСОС | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:21/ O1010207:1A | TS-F-03:22/ O1010207:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -D | 17XSAM071D |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-GG-VD-BD17617P071001_SH.6 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.12 | 17-MC-DCS-003 | TS-F-03 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071D | 17-P-071D ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:23/ O1010207:2A | TS-F-03:24/ O1010207:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -D | 17XSRM071D |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-GG-VD-BD17617P071001_SH.6 | DCS_DI_05 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.13 | 17-MC-DCS-003 | TS-F-03 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071D | 17-P-071D МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:25/ O1010207:3A | TS-F-03:26/ O1010207:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -D | 17XYSPM071D |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-GG-VD-BD17617P071001_SH.6 | DCS_DO_04 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.19 | 17-MC-DCS-003 | TS-G-03 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071D | 17-P-071D СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:20/ O1010213:3A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -D | 17XYSTM071D |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-GG-VD-BD17617P071001_SH.6 | DCS_DO_04 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.21 | 17-MC-DCS-003 | TS-G-03 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CW Circulation Pump 7-P-071D | 17-P-071D ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:22/ O1010213:4A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -E | 17XSM071E |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-GG-VD-BD17617P071001_SH.7 | DCS_DI_05 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.01 | 17-MC-DCS-003 | TS-F-04 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071E RUNNING | P071E ЦИРКУЛЯЦИОННЫЙ НАСОС | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:1/ O1010207:10A | TS-F-04:2/ O1010207:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -E | 17XSAM071E |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-GG-VD-BD17617P071001_SH.7 | DCS_DI_05 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.02 | 17-MC-DCS-003 | TS-F-04 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071E AVAILABLE | 17-P-071E ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:3/ O1010207:11A | TS-F-04:4/ O1010207:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -E | 17XSRM071E |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-GG-VD-BD17617P071001_SH.7 | DCS_DI_05 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.03 | 17-MC-DCS-003 | TS-F-04 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071E LOCAL/REMOTE | 17-P-071E МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:5/ O1010207:12A | TS-F-04:6/ O1010207:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -E | 17XYSPM071E |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-GG-VD-BD17617P071001_SH.7 | DCS_DO_04 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.05 | 17-MC-DCS-003 | TS-G-04 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071E STOP | 17-P-071E СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:6/ O1010213:9A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -E | 17XYSTM071E |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-GG-VD-BD17617P071001_SH.7 | DCS_DO_04 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.07 | 17-MC-DCS-003 | TS-G-04 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071E START | 17-P-071E ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:8/ O1010213:10A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -F | 17XSM071F |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-GG-VD-BD17617P071001_SH.8 | DCS_DI_05 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.04 | 17-MC-DCS-003 | TS-F-04 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071F RUNNING | P071F ЦИРКУЛЯЦИОННЫЙ НАСОС | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:7/ O1010207:13A | TS-F-04:8/ O1010207:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -F | 17XSAM071F |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-GG-VD-BD17617P071001_SH.8 | DCS_DI_05 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.05 | 17-MC-DCS-003 | TS-F-04 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071F AVAILABLE | 17-P-071F ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:9/ O1010207:14A | TS-F-04:10/ O1010207:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -F | 17XSRM071F |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-GG-VD-BD17617P071001_SH.8 | DCS_DI_05 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.06 | 17-MC-DCS-003 | TS-F-04 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071F LOCAL/REMOTE | 17-P-071F МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:11/ O1010207:15A | TS-F-04:12/ O1010207:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -F | 17XYSPM071F |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-GG-VD-BD17617P071001_SH.8 | DCS_DO_04 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.09 | 17-MC-DCS-003 | TS-G-04 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071F STOP | 17-P-071F СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:10/ O1010213:11A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -F | 17XYSTM071F |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-GG-VD-BD17617P071001_SH.8 | DCS_DO_04 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.11 | 17-MC-DCS-003 | TS-G-04 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071F START | 17-P-071F ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:12/ O1010213:12A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -G | 17XSM071G |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-GG-VD-BD17617P071001_SH.9 | DCS_DI_05 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.07 | 17-MC-DCS-003 | TS-F-04 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071G RUNNING | P071G ЦИРКУЛЯЦИОННЫЙ НАСОС | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:13/ O1010207:16A | TS-F-04:14/ O1010207:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -G | 17XSAM071G |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-GG-VD-BD17617P071001_SH.9 | DCS_DI_05 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.08 | 17-MC-DCS-003 | TS-F-04 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071G AVAILABLE | 17-P-071G ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:15/ O1010207:17A | TS-F-04:16/ O1010207:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -G | 17XSRM071G |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-GG-VD-BD17617P071001_SH.9 | DCS_DI_05 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.09 | 17-MC-DCS-003 | TS-F-04 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071G LOCAL/REMOTE | 17-P-071G МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:17/ O1010207:18A | TS-F-04:18/ O1010207:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -G | 17XYSPM071G |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-GG-VD-BD17617P071001_SH.9 | DCS_DO_04 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.13 | 17-MC-DCS-003 | TS-G-04 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071G STOP | 17-P-071G СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:14/ O1010213:13A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -071 -G | 17XYSTM071G |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-GG-VD-BD17617P071001_SH.9 | DCS_DO_04 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.15 | 17-MC-DCS-003 | TS-G-04 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-071G START | 17-P-071G ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:16/ O1010213:14A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -A | 17STM071LKA |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Speed Transmitter | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_AI_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.01 | 17-MC-DCS-006 | TS-Q-01 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U1 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Motor | 17-L-071-K-071A СКОРОСТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1500 | rpm | [5 empty] | TS-Q-01:1/ O1010012R_U1:3 | TS-Q-01:2/ O1010012R_U1:4 |  |  | O1010012R:1A/ O1010012R_U1:5 | O1010012R:1C/ O1010012R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -A | 17XYSYM071LKA |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Motor Speed Set-Point signal | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_AO_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.09 | 17-MC-DCS-006 | TS-Q-01 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U1 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 1 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Motor | 17-L-071-K-071A СКОРОСТЬ ДВИГ-ЛЯ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:17/ O1010104R_U1:3 | TS-Q-01:18/ O1010104R_U1:4 |  |  | O1010104R:1A/ O1010104R_U1:5 | O1010104R:1C/ O1010104R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -A | 17XSAM071LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.08 | 17-MC-DCS-003 | TS-F-02 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Motor | 17-L-071-K-071A ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:15/ O1010206:8A | TS-F-02:16/ O1010206:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -A | 17XSRM071LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.09 | 17-MC-DCS-003 | TS-F-02 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Motor | 17-L-071-K-071A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:17/ O1010206:9A | TS-F-02:18/ O1010206:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -A | 17XSBM071LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.18 | 17-MC-DCS-005 | TS-F-02 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Motor | 17-P-071LK -A В РАБОТЕ ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:35/ O1010209:17A | TS-F-02:36/ O1010209:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -A | 17XSFM071LKA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.19 | 17-MC-DCS-005 | TS-F-02 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Motor | P071LKA ВЕНТИЛЯТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:37/ O1010209:18A | TS-F-02:38/ O1010209:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -A | 17XYSPM071LKA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.01 | 17-MC-DCS-003 | TS-G-02 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Motor | 17-L-071-K-071A СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:2/ O1010212:13A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -A | 17XYSTBM071LKA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Backward Start Command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.03 | 17-MC-DCS-003 | TS-G-02 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Motor | 17-P-071LK -A ПУСК ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | BKWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:4/ O1010212:14A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -A | 17XYSTFM071LKA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Forward Start Command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.05 | 17-MC-DCS-003 | TS-G-02 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071A Motor | 17-P-071LK -A ПУСК ВПЕРЕД | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | FRWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:6/ O1010212:15A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -B | 17STM071LKB |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Speed Transmitter | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_AI_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.02 | 17-MC-DCS-006 | TS-Q-01 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U2 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Motor | 17-L-071-K-071B СКОРОСТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1500 | rpm | [5 empty] | TS-Q-01:3/ O1010012R_U2:3 | TS-Q-01:4/ O1010012R_U2:4 |  |  | O1010012R:2A/ O1010012R_U2:5 | O1010012R:2C/ O1010012R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -B | 17XYSYM071LKB |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Motor Speed Set-Point signal | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_AO_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.10 | 17-MC-DCS-006 | TS-Q-01 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U2 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 2 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Motor | 17L071K071B СКОРОСТЬ ДВИГАТЕЛЯ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:19/ O1010104R_U2:3 | TS-Q-01:20/ O1010104R_U2:4 |  |  | O1010104R:2A/ O1010104R_U2:5 | O1010104R:2C/ O1010104R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -B | 17XSAM071LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.10 | 17-MC-DCS-003 | TS-F-02 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Motor | 17-L-071-K-071B ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:19/ O1010206:10A | TS-F-02:20/ O1010206:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -B | 17XSRM071LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.11 | 17-MC-DCS-003 | TS-F-02 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Motor | 17-L-071-K-071B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:21/ O1010206:11A | TS-F-02:22/ O1010206:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -B | 17XSBM071LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.20 | 17-MC-DCS-005 | TS-F-02 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Motor | 17-P-071LK -B ДВИГАТЕЛЬ ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:39/ O1010209:19A | TS-F-02:40/ O1010209:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -B | 17XSFM071LKB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-017BL02 | 24 Pair | Pr.21 | 17-MC-DCS-005 | TS-F-02 | 41 | 42 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Motor | P071LKB ВЕНТИЛЯТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:41/ O1010209:20A | TS-F-02:42/ O1010209:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -B | 17XYSPM071LKB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.07 | 17-MC-DCS-003 | TS-G-02 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Motor | 17-L-071-K-071B СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:8/ O1010212:16A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -B | 17XYSTBM071LKB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Backward Start Command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.09 | 17-MC-DCS-003 | TS-G-02 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Motor | 17-L-071-K-071B ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | BKWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:10/ O1010212:17A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -B | 17XYSTFM071LKB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Forward Start Command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.11 | 17-MC-DCS-003 | TS-G-02 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071B Motor | 17-L-071-K-071B ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | FRWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:12/ O1010212:18A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -C | 17STM071LKC |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Speed Transmitter | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_AI_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.03 | 17-MC-DCS-006 | TS-Q-01 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U3 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Motor | 17-L-071-K-071C СКОРОСТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1500 | rpm | [5 empty] | TS-Q-01:5/ O1010012R_U3:3 | TS-Q-01:6/ O1010012R_U3:4 |  |  | O1010012R:3A/ O1010012R_U3:5 | O1010012R:3C/ O1010012R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -C | 17XYSYM071LKC |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Motor Speed Set-Point signal | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_AO_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.11 | 17-MC-DCS-006 | TS-Q-01 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U3 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 3 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Motor | 17L071-K-071C СКОРОСТЬ ДВИГАТЕЛЯ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:21/ O1010104R_U3:3 | TS-Q-01:22/ O1010104R_U3:4 |  |  | O1010104R:3A/ O1010104R_U3:5 | O1010104R:3C/ O1010104R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -C | 17XSAM071LKC |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.12 | 17-MC-DCS-003 | TS-F-02 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Motor | 17-L-071-K-071C ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:23/ O1010206:12A | TS-F-02:24/ O1010206:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -C | 17XSRM071LKC |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.13 | 17-MC-DCS-003 | TS-F-02 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Motor | 17-L-071-K-071C МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:25/ O1010206:13A | TS-F-02:26/ O1010206:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -C | 17XSBM071LKC |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.01 | 17-MC-DCS-005 | TS-F-03 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Motor | 17P-071LK -C ДВИГАТЕЛЬ ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:1/ O1010209:21A | TS-F-03:2/ O1010209:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -C | 17XSFM071LKC |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.02 | 17-MC-DCS-005 | TS-F-03 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Motor | P071LKC ВЕНТИЛЯТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:3/ O1010209:22A | TS-F-03:4/ O1010209:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -C | 17XYSPM071LKC |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.13 | 17-MC-DCS-003 | TS-G-02 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Motor | 17-L-071-K-071C СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:14/ O1010212:19A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -C | 17XYSTBM071LKC |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Backward Start Command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.15 | 17-MC-DCS-003 | TS-G-02 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Motor | 17-L-071-K-071C ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | BKWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:16/ O1010212:20A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -C | 17XYSTFM071LKC |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Forward Start Command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.17 | 17-MC-DCS-003 | TS-G-02 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071C Motor | 17-L-071-K-071C ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | FRWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:18/ O1010212:21A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -D | 17STM071LKD |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Speed Transmitter | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_AI_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.04 | 17-MC-DCS-006 | TS-Q-01 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U4 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Motor | 17-L-071-K-071D СКОРОСТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1500 | rpm | [5 empty] | TS-Q-01:7/ O1010012R_U4:3 | TS-Q-01:8/ O1010012R_U4:4 |  |  | O1010012R:4A/ O1010012R_U4:5 | O1010012R:4C/ O1010012R_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -D | 17XYSYM071LKD |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Motor Speed Set-Point signal | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_AO_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.12 | 17-MC-DCS-006 | TS-Q-01 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U4 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 4 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Motor | 17L071-K-071D СКОРОСТЬ ДВИГАТЕЛЯ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:23/ O1010104R_U4:3 | TS-Q-01:24/ O1010104R_U4:4 |  |  | O1010104R:4A/ O1010104R_U4:5 | O1010104R:4C/ O1010104R_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -D | 17XSAM071LKD |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.14 | 17-MC-DCS-003 | TS-F-02 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Motor | 17-L-071-K-071D ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:27/ O1010206:14A | TS-F-02:28/ O1010206:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -D | 17XSRM071LKD |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.15 | 17-MC-DCS-003 | TS-F-02 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Motor | 17-L-071-K-071D МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:29/ O1010206:15A | TS-F-02:30/ O1010206:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -D | 17XSBM071LKD |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.03 | 17-MC-DCS-005 | TS-F-03 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Motor | 17-P-071LK -D ДВИГАТЕЛЬ ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:5/ O1010209:23A | TS-F-03:6/ O1010209:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -D | 17XSFM071LKD |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.04 | 17-MC-DCS-005 | TS-F-03 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Motor | P071LKD ВЕНТИЛЯТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:7/ O1010209:24A | TS-F-03:8/ O1010209:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -D | 17XYSPM071LKD |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.19 | 17-MC-DCS-003 | TS-G-02 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Motor | 17-L-071-K-071D СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:20/ O1010212:22A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -D | 17XYSTBM071LKD |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Backward Start Command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.21 | 17-MC-DCS-003 | TS-G-02 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Motor | 17-P-071LK -D ДВИГАТЕЛЬ ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | BKWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:22/ O1010212:23A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -D | 17XYSTFM071LKD |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Forward Start Command | 4124-FY-VD-BD17317L07100001_SH.1 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.23 | 17-MC-DCS-003 | TS-G-02 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071D Motor | 17-P-071LK -D ДВИГАТЕЛЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | FRWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:24/ O1010212:24A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -E | 17STM071LKE |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Speed Transmitter | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_AI_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.05 | 17-MC-DCS-006 | TS-Q-01 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U5 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Motor | 17-L-071-K-071E СКОРОСТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1500 | rpm | [5 empty] | TS-Q-01:9/ O1010012R_U5:3 | TS-Q-01:10/ O1010012R_U5:4 |  |  | O1010012R:5A/ O1010012R_U5:5 | O1010012R:5C/ O1010012R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -E | 17XYSYM071LKE |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Motor Speed Set-Point signal | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_AO_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.13 | 17-MC-DCS-006 | TS-Q-01 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U5 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 5 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Motor | 17L071K071E СКОРОСТЬ ДВИГАТЕЛЯ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:25/ O1010104R_U5:3 | TS-Q-01:26/ O1010104R_U5:4 |  |  | O1010104R:5A/ O1010104R_U5:5 | O1010104R:5C/ O1010104R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -E | 17XSAM071LKE |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.16 | 17-MC-DCS-003 | TS-F-02 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Motor | 17-L-071-K-071E ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:31/ O1010206:16A | TS-F-02:32/ O1010206:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -E | 17XSRM071LKE |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.17 | 17-MC-DCS-003 | TS-F-02 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Motor | 17-L-071-K-071E МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:33/ O1010206:17A | TS-F-02:34/ O1010206:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -E | 17XSBM071LKE |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.05 | 17-MC-DCS-005 | TS-F-03 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Motor | 17-P-071LK -E ДВИГАТЕЛЬ ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:9/ O1010209:25A | TS-F-03:10/ O1010209:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -E | 17XSFM071LKE |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.06 | 17-MC-DCS-005 | TS-F-03 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Motor | P071LKE ВЕНТИЛЯТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:11/ O1010209:26A | TS-F-03:12/ O1010209:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -E | 17XYSPM071LKE |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-006BL02 | 30 Core | C.25 | 17-MC-DCS-003 | TS-G-02 | 25 | 26 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Motor | 17-L-071-K-071E СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-02:26/ O1010212:25A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -E | 17XYSTBM071LKE |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Backward Start Command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.09 | 17-MC-DCS-003 | TS-G-08 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Motor | 17-P-071LK -E ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | BKWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:10/ O1010214:23A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -E | 17XYSTFM071LKE |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Forward Start Command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.11 | 17-MC-DCS-003 | TS-G-08 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071E Motor | 17-P-071LK -E ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | FRWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:12/ O1010214:24A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -F | 17STM071LKF |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Speed Transmitter | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_AI_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.06 | 17-MC-DCS-006 | TS-Q-01 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U6 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Motor | 17-L-071-K-071F СКОРОСТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1500 | rpm | [5 empty] | TS-Q-01:11/ O1010012R_U6:3 | TS-Q-01:12/ O1010012R_U6:4 |  |  | O1010012R:6A/ O1010012R_U6:5 | O1010012R:6C/ O1010012R_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -F | 17XYSYM071LKF |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Motor Speed Set-Point signal | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_AO_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.14 | 17-MC-DCS-006 | TS-Q-01 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U6 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 6 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Motor | 17L071K071F СКОРОСТЬ ДВИГАТЕЛЯ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:27/ O1010104R_U6:3 | TS-Q-01:28/ O1010104R_U6:4 |  |  | O1010104R:6A/ O1010104R_U6:5 | O1010104R:6C/ O1010104R_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -F | 17XSAM071LKF |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.18 | 17-MC-DCS-003 | TS-F-02 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Motor | 17-L-071-K-071F ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:35/ O1010206:18A | TS-F-02:36/ O1010206:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -F | 17XSRM071LKF |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.19 | 17-MC-DCS-003 | TS-F-02 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Motor | 17-L-071-K-071F МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:37/ O1010206:19A | TS-F-02:38/ O1010206:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -F | 17XSBM071LKF |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.07 | 17-MC-DCS-005 | TS-F-03 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Motor | 17-P-071LK -F ДВИГАТЕЛЬ ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:13/ O1010209:27A | TS-F-03:14/ O1010209:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -F | 17XSFM071LKF |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.08 | 17-MC-DCS-005 | TS-F-03 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Motor | P071LKF ВЕНТИЛЯТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:15/ O1010209:28A | TS-F-03:16/ O1010209:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -F | 17XYSPM071LKF |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.01 | 17-MC-DCS-003 | TS-G-03 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Motor | 17-L-071-K-071F СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:2/ O1010212:26A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -F | 17XYSTBM071LKF |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Backward Start Command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.13 | 17-MC-DCS-003 | TS-G-08 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Motor | 17-P-071LK -F ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | BKWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:14/ O1010214:25A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -F | 17XYSTFM071LKF |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Forward Start Command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.15 | 17-MC-DCS-003 | TS-G-08 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071F Motor | 17-P-071LK -F ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | FRWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:16/ O1010214:26A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -G | 17STM071LKG |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Speed Transmitter | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_AI_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.07 | 17-MC-DCS-006 | TS-Q-01 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U7 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Motor | 17-L-071-K-071G СКОРОСТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1500 | rpm | [5 empty] | TS-Q-01:13/ O1010012R_U7:3 | TS-Q-01:14/ O1010012R_U7:4 |  |  | O1010012R:7A/ O1010012R_U7:5 | O1010012R:7C/ O1010012R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -G | 17XYSYM071LKG |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Motor Speed Set-Point signal | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_AO_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.15 | 17-MC-DCS-006 | TS-Q-01 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U7 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 7 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Motor | 17L071K071G СКОРОСТЬ ДВИГАТЕЛЯ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:29/ O1010104R_U7:3 | TS-Q-01:30/ O1010104R_U7:4 |  |  | O1010104R:7A/ O1010104R_U7:5 | O1010104R:7C/ O1010104R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -G | 17XSAM071LKG |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.20 | 17-MC-DCS-003 | TS-F-02 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Motor | 17-L-071-K-071G ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:39/ O1010206:20A | TS-F-02:40/ O1010206:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -G | 17XSRM071LKG |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.21 | 17-MC-DCS-003 | TS-F-02 | 41 | 42 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Motor | 17-L-071-K-071G МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:41/ O1010206:21A | TS-F-02:42/ O1010206:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -G | 17XSBM071LKG |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.09 | 17-MC-DCS-005 | TS-F-03 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Motor | 17-P-071LK -G ДВИГАТЕЛЬ ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:17/ O1010209:29A | TS-F-03:18/ O1010209:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -G | 17XSFM071LKG |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.10 | 17-MC-DCS-005 | TS-F-03 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Motor | P071LKG ВЕНТИЛЯТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:19/ O1010209:30A | TS-F-03:20/ O1010209:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -G | 17XYSPM071LKG |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.03 | 17-MC-DCS-003 | TS-G-03 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Motor | 17-L-071-K-071G СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:4/ O1010212:27A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -G | 17XYSTBM071LKG |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Backward Start Command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.17 | 17-MC-DCS-003 | TS-G-08 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Motor | 17-P-071LK -G ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | BKWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:18/ O1010214:27A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -G | 17XYSTFM071LKG |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Forward Start Command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.19 | 17-MC-DCS-003 | TS-G-08 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071G Motor | 17-P-071LK -G ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | FRWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:20/ O1010214:28A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -H | 17STM071LKH |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Speed Transmitter | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_AI_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.08 | 17-MC-DCS-006 | TS-Q-01 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U8 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Motor | 17-L-071-K-071H СКОРОСТЬ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1500 | rpm | [5 empty] | TS-Q-01:15/ O1010012R_U8:3 | TS-Q-01:16/ O1010012R_U8:4 |  |  | O1010012R:8A/ O1010012R_U8:5 | O1010012R:8C/ O1010012R_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -H | 17XYSYM071LKH |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Motor Speed Set-Point signal | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_AO_02 | MCC |  | 17-B-AD-N-001BL02 | 24 Pair | Pr.16 | 17-MC-DCS-006 | TS-Q-01 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U8 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 8 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Motor | 17L071K071H СКОРОСТЬ ДВИГАТЕЛЯ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:31/ O1010104R_U8:3 | TS-Q-01:32/ O1010104R_U8:4 |  |  | O1010104R:8A/ O1010104R_U8:5 | O1010104R:8C/ O1010104R_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -H | 17XSAM071LKH |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-002BL02 | 24 Pair | Pr.22 | 17-MC-DCS-003 | TS-F-02 | 43 | 44 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Motor | 17-L-071-K-071H ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-02:43/ O1010206:22A | TS-F-02:44/ O1010206:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -H | 17XSRM071LKH |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.01 | 17-MC-DCS-003 | TS-F-03 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010206 | TUA711-DIO32 | 17-SC-DCS-001/O1010206/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010206 | 7 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Motor | 17-L-071-K-071H МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:1/ O1010206:23A | TS-F-03:2/ O1010206:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -H | 17XSBM071LKH |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.11 | 17-MC-DCS-005 | TS-F-03 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Motor | 17L071K071H ДВИГАТЕЛЬ ОБРАТНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:21/ O1010209:31A | TS-F-03:22/ O1010209:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -H | 17XSFM071LKH |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DI_03 | MCC |  | 17-I-DD-N-018BL02 | 24 Pair | Pr.12 | 17-MC-DCS-005 | TS-F-03 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010209 | TUA711-DIO32 | 17-SC-DCS-001/O1010209/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010209 | 10 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Motor | P071LKH ВЕНТИЛЯТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:23/ O1010209:32A | TS-F-03:24/ O1010209:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -H | 17XYSPM071LKH |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.05 | 17-MC-DCS-003 | TS-G-03 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010212 | TUA711-DIO32 | 17-SC-DCS-001/O1010212/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010212 | 13 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Motor | 17-L-071-K-071H СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:6/ O1010212:28A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -H | 17XYSTBM071LKH |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Backward Start Command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.21 | 17-MC-DCS-003 | TS-G-08 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Motor | 17-P-071LK -H ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | BKWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:22/ O1010214:29A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LK -H | 17XYSTFM071LKH |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Forward Start Command | 4124-FY-VD-BD17317L07100001_SH.2 | DCS_DO_03 | MCC |  | 17-I-CD-N-018BL02 | 30 Core | C.23 | 17-MC-DCS-003 | TS-G-08 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-071-K-071H Motor | 17-P-071LK -H ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | FRWRD | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-08:24/ O1010214:30A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -A | 17XSM071LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.01 | 17-MC-DCS-004 | TS-O-06 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071A 92.5% H2SO4 Injection Pump | PM071A НАСОС H2SO4 | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:1/ O1011106:22A | TS-O-06:2/ O1011106:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -A | 17XSAM071LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.02 | 17-MC-DCS-004 | TS-O-06 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071A 92.5% H2SO4 Injection Pump | 17L073PM071A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:3/ O1011106:23A | TS-O-06:4/ O1011106:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -A | 17XSRM071LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.03 | 17-MC-DCS-004 | TS-O-06 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071A 92.5% H2SO4 Injection Pump | 17L073PM071A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:5/ O1011106:24A | TS-O-06:6/ O1011106:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -A | 17XYSPM071LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.09 | 17-MC-DCS-004 | TS-O-02 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071A 92.5% H2SO4 Injection Pump | 17L073PM071A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:10/ O1011205:19A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -A | 17XYSTM071LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17217L07300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.11 | 17-MC-DCS-004 | TS-O-02 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071A 92.5% H2SO4 Injection Pump | 17L073PM071A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:12/ O1011205:20A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -B | 17XSM071LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.04 | 17-MC-DCS-004 | TS-O-06 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071B 92.5% H2SO4 Injection Pump | PM071B НАСОС H2SO4 | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:7/ O1011106:25A | TS-O-06:8/ O1011106:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -B | 17XSAM071LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.05 | 17-MC-DCS-004 | TS-O-06 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071B 92.5% H2SO4 Injection Pump | 17L073PM071B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:9/ O1011106:26A | TS-O-06:10/ O1011106:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -B | 17XSRM071LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300001 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.06 | 17-MC-DCS-004 | TS-O-06 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071B 92.5% H2SO4 Injection Pump | 17L073PM071B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:11/ O1011106:27A | TS-O-06:12/ O1011106:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -B | 17XYSPM071LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.13 | 17-MC-DCS-004 | TS-O-02 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071B 92.5% H2SO4 Injection Pump | 17L073PM071B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:14/ O1011205:21A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -071LP -B | 17XYSTM071LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17217L07300001 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.15 | 17-MC-DCS-004 | TS-O-02 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-071B 92.5% H2SO4 Injection Pump | 17L073PM071B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:16/ O1011205:22A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -A | 17TSHM072A |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21707005 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.17 | 17-MC-DCS-001 | TS-F-02 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U1 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072A | 17-P-072A ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-02:33/ O1010203_U1:3 | TS-F-02:34/ O1010203_U1:4 |  |  | O1010203:1A/ O1010203_U1:5 | O1010203:1B/ O1010203_U1:6 | [6 empty] | 1A | 1B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -A | 17XSLM072A |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21707005 | DCS_DI_04 | Field |  | 17-C-DD-N-001FL07 | 24 Pair | Pr.18 | 17-MC-DCS-001 | TS-F-02 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U28 | KFD2-ER-1.W.LB | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072A | 17-P-072A СИГНАЛИЗ УТЕЧКИ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-02:35/ O1010203_U28:3 | TS-F-02:36/ O1010203_U28:1 |  |  | O1010203:28A/ O1010203_U28:7 | O1010203:28B/ O1010203_U28:8 | [6 empty] | 28A | 28B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -A | 17XSM072A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21707005 | DCS_DI_03 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.14 | 17-MC-DCS-003 | TS-F-03 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072A | P072A НАСОС СТОЧНЫХ ВОД | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:27/ O1010207:4A | TS-F-03:28/ O1010207:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -A | 17XSAM072A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21707005 | DCS_DI_03 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.15 | 17-MC-DCS-003 | TS-F-03 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072A | 17-P-072A ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:29/ O1010207:5A | TS-F-03:30/ O1010207:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -A | 17XSRM072A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21707005 | DCS_DI_03 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.16 | 17-MC-DCS-003 | TS-F-03 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072A | 17-P-072A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:31/ O1010207:6A | TS-F-03:32/ O1010207:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -A | 17XYSPM072A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21707005 | DCS_DO_03 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.23 | 17-MC-DCS-003 | TS-G-03 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072A | 17-P-072A СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:24/ O1010213:5A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -A | 17XYSTM072A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21707005 | DCS_DO_03 | MCC |  | 17-I-CD-N-007BL02 | 30 Core | C.25 | 17-MC-DCS-003 | TS-G-03 | 25 | 26 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072A | 17-P-072A ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-03:26/ O1010213:6A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -B | 17XSM072B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21707005 | DCS_DI_03 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.17 | 17-MC-DCS-003 | TS-F-03 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072B | P072B НАСОС СТОЧНЫХ ВОД | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:33/ O1010207:7A | TS-F-03:34/ O1010207:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -B | 17XSAM072B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21707005 | DCS_DI_03 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.18 | 17-MC-DCS-003 | TS-F-03 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072B | 17-P-072B ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:35/ O1010207:8A | TS-F-03:36/ O1010207:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -B | 17XSRM072B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21707005 | DCS_DI_03 | MCC |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.19 | 17-MC-DCS-003 | TS-F-03 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072B | 17-P-072B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-03:37/ O1010207:9A | TS-F-03:38/ O1010207:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -B | 17XYSPM072B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21707005 | DCS_DO_03 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.01 | 17-MC-DCS-003 | TS-G-04 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072B | 17-P-072B СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:2/ O1010213:7A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -B | 17XYSTM072B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21707005 | DCS_DO_03 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.03 | 17-MC-DCS-003 | TS-G-04 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072B | 17-P-072B ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:4/ O1010213:8A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -B | 17TSHM072B |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21707005 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.13 | 17-MC-DCS-002 | TS-R-03 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U5 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072B | 17-P-072В ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-03:25/ O1011104_U5:3 | TS-R-03:26/ O1011104_U5:4 |  |  | O1011104:5A/ O1011104_U5:5 | O1011104:5B/ O1011104_U5:6 | [6 empty] | 5A | 5B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072 -B | 17XSLM072B |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21707005 | DCS_DI_04 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.14 | 17-MC-DCS-002 | TS-R-03 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U32 | KFD2-ER-1.W.LB | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Motor for Filter 17-P-072B | 17-P-072В СИГНАЛИЗ УТЕЧКИ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-03:27/ O1011104_U32:3 | TS-R-03:28/ O1011104_U32:1 |  |  | O1011104:32A/ O1011104_U32:7 | O1011104:32B/ O1011104_U32:8 | [6 empty] | 32A | 32B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -A | 17XSM072LA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GF-VD-BD17717L072003 | DCS_DI_03 | MCC |  | 17-I-DD-N-016BL02 | 12 Pair | Pr.04 | 17-MC-DCS-004 | TS-P-06 | 7 | 8 |  | 24 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-A | L072A ФИЛЬТР САМОПРОМЫВНОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-06:7/ O1011110:19A | TS-P-06:8/ O1011110:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -A | 17XSAM072LA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GF-VD-BD17717L072003 | DCS_DI_03 | MCC |  | 17-I-DD-N-016BL02 | 12 Pair | Pr.05 | 17-MC-DCS-004 | TS-P-06 | 9 | 10 |  | 24 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-A | 17-L-072-A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-06:9/ O1011110:20A | TS-P-06:10/ O1011110:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -A | 17XSRM072LA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-GF-VD-BD17717L072003 | DCS_DI_03 | MCC |  | 17-I-DD-N-016BL02 | 12 Pair | Pr.06 | 17-MC-DCS-004 | TS-P-06 | 11 | 12 |  | 24 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-A | 17-L-072-A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-06:11/ O1011110:21A | TS-P-06:12/ O1011110:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -A | 17XYSPM072LA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GF-VD-BD17717L072003 | DCS_DO_03 | MCC |  | 17-I-CD-N-017BL02 | 16 Core | C.01 | 17-MC-DCS-004 | TS-P-07 | 1 | 2 |  | 16 | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-A | 17-L-072-A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-07:2/ O1011208:5A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -A | 17XYSTM072LA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GF-VD-BD17717L072003 | DCS_DO_03 | MCC |  | 17-I-CD-N-017BL02 | 16 Core | C.03 | 17-MC-DCS-004 | TS-P-07 | 3 | 4 |  | 16 | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-A | 17-L-072-A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-07:4/ O1011208:6A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -B | 17XSM072LB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GF-VD-BD17717L072003 | DCS_DI_03 | MCC |  | 17-I-DD-N-016BL02 | 12 Pair | Pr.07 | 17-MC-DCS-004 | TS-P-06 | 13 | 14 |  | 24 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-B | L072B ФИЛЬТР САМОПРОМЫВНОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-06:13/ O1011110:22A | TS-P-06:14/ O1011110:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -B | 17XSAM072LB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GF-VD-BD17717L072003 | DCS_DI_03 | MCC |  | 17-I-DD-N-016BL02 | 12 Pair | Pr.08 | 17-MC-DCS-004 | TS-P-06 | 15 | 16 |  | 24 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-B | 17-L-072-B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-06:15/ O1011110:23A | TS-P-06:16/ O1011110:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -B | 17XSRM072LB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-GF-VD-BD17717L072003 | DCS_DI_03 | MCC |  | 17-I-DD-N-016BL02 | 12 Pair | Pr.09 | 17-MC-DCS-004 | TS-P-06 | 17 | 18 |  | 24 | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-B | 17-L-072-B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-06:17/ O1011110:24A | TS-P-06:18/ O1011110:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -B | 17XYSPM072LB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GF-VD-BD17717L072003 | DCS_DO_03 | MCC |  | 17-I-CD-N-017BL02 | 16 Core | C.05 | 17-MC-DCS-004 | TS-P-07 | 5 | 6 |  | 16 | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-B | 17-L-072-B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-07:6/ O1011208:7A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072L -B | 17XYSTM072LB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GF-VD-BD17717L072003 | DCS_DO_03 | MCC |  | 17-I-CD-N-017BL02 | 16 Core | C.07 | 17-MC-DCS-004 | TS-P-07 | 7 | 8 |  | 16 | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | ROTARY FILTER MOTOR 17-L-072-B | 17-L-072-B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-07:8/ O1011208:8A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -A | 17XSM072LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300002 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.07 | 17-MC-DCS-004 | TS-O-06 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072A Corrosion Inhibitor Injection Pump | PM072A НАСОС ИНГИБ. КОРРОЗИИ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:13/ O1011106:28A | TS-O-06:14/ O1011106:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -A | 17XSAM072LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300002 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.08 | 17-MC-DCS-004 | TS-O-06 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072A Corrosion Inhibitor Injection Pump | 17L073PM072A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:15/ O1011106:29A | TS-O-06:16/ O1011106:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -A | 17XSRM072LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300002 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.09 | 17-MC-DCS-004 | TS-O-06 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072A Corrosion Inhibitor Injection Pump | 17L073PM072A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:17/ O1011106:30A | TS-O-06:18/ O1011106:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -A | 17XYSTM072LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor START command | 4124-FY-VD-BD17217L07300002 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.17 | 17-MC-DCS-004 | TS-O-02 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072A Corrosion Inhibitor Injection Pump | 17L073PM072A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:18/ O1011205:23A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -A | 17XYSPM072LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300002 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.19 | 17-MC-DCS-004 | TS-O-02 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072A Corrosion Inhibitor Injection Pump | 17L073PM072A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:20/ O1011205:24A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -B | 17XSM072LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300002 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.10 | 17-MC-DCS-004 | TS-O-06 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072B Corrosion Inhibitor Injection Pump | PM072B НАСОС ИНГИБ. КОРРОЗИИ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:19/ O1011106:31A | TS-O-06:20/ O1011106:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -B | 17XSAM072LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300002 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.11 | 17-MC-DCS-004 | TS-O-06 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011106 | TUA711-DIO32 | 17-SC-DCS-002/O1011106/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011106 | 7 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072B Corrosion Inhibitor Injection Pump | 17L073PM072B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:21/ O1011106:32A | TS-O-06:22/ O1011106:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -B | 17XSRM072LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300002 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.12 | 17-MC-DCS-004 | TS-O-06 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072B Corrosion Inhibitor Injection Pump | 17L073PM072B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:23/ O1011107:1A | TS-O-06:24/ O1011107:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -B | 17XYSPM072LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300002 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.21 | 17-MC-DCS-004 | TS-O-02 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072B Corrosion Inhibitor Injection Pump | 17L073PM072B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:22/ O1011205:25A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -072LP -B | 17XYSTM072LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor START command | 4124-FY-VD-BD17217L07300002 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.01 | 17-MC-DCS-004 | TS-P-03 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-072B Corrosion Inhibitor Injection Pump | 17L073PM072B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:2/ O1011206:14A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -A | 17XSM073A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P073135 | DCS_DI_03 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.10 | 17-MC-DCS-003 | TS-F-04 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric motor 17-PM-073A | P073A АВАРИЙНЫЙ НАСОС | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:19/ O1010207:19A | TS-F-04:20/ O1010207:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -A | 17XSAM073A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P073135 | DCS_DI_03 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.11 | 17-MC-DCS-003 | TS-F-04 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric motor 17-PM-073A | 17-P-073A ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:21/ O1010207:20A | TS-F-04:22/ O1010207:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -A | 17XSRM073A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P073135 | DCS_DI_03 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.12 | 17-MC-DCS-003 | TS-F-04 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric motor 17-PM-073A | 17-P-073A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:23/ O1010207:21A | TS-F-04:24/ O1010207:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -A | 17XYSPM073A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P073135 | DCS_DO_03 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.17 | 17-MC-DCS-003 | TS-G-04 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric motor 17-PM-073A | 17-P-073A СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:18/ O1010213:15A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -A | 17XYSTM073A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P073135 | DCS_DO_03 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.19 | 17-MC-DCS-003 | TS-G-04 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Electric motor 17-PM-073A | 17-P-073A ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:20/ O1010213:16A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -B | 17XSM073B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P073135 | DCS_DI_03 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.13 | 17-MC-DCS-003 | TS-F-04 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Emergency CW Pump 17-P-073B | P073B АВАРИЙНЫЙ НАСОС | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:25/ O1010207:22A | TS-F-04:26/ O1010207:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -B | 17XSAM073B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P073135 | DCS_DI_03 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.14 | 17-MC-DCS-003 | TS-F-04 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Emergency CW Pump 17-P-073B | 17-P-073B ДОСТУПНО | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:27/ O1010207:23A | TS-F-04:28/ O1010207:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -B | 17XSRM073B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P073135 | DCS_DI_03 | MCC |  | 17-I-DD-N-004BL02 | 24 Pair | Pr.15 | 17-MC-DCS-003 | TS-F-04 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Emergency CW Pump 17-P-073B | 17-P-073B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:29/ O1010207:24A | TS-F-04:30/ O1010207:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -B | 17XYSPM073B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P073135 | DCS_DO_03 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.21 | 17-MC-DCS-003 | TS-G-04 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Emergency CW Pump 17-P-073B | 17-P-073B СТОП | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:22/ O1010213:17A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073 -B | 17XYSTM073B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P073135 | DCS_DO_03 | MCC |  | 17-I-CD-N-008BL02 | 30 Core | C.23 | 17-MC-DCS-003 | TS-G-04 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Emergency CW Pump 17-P-073B | 17-P-073B ПУСК | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-04:24/ O1010213:18A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -A | 17XSM073LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300003 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.13 | 17-MC-DCS-004 | TS-O-06 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073A Dispersant Injection Pump | PM073A НАСОС ДИСПЕРСАНТА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:25/ O1011107:2A | TS-O-06:26/ O1011107:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -A | 17XSAM073LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300003 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.14 | 17-MC-DCS-004 | TS-O-06 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073A Dispersant Injection Pump | 17L073PM073A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:27/ O1011107:3A | TS-O-06:28/ O1011107:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -A | 17XSRM073LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300003 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.15 | 17-MC-DCS-004 | TS-O-06 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073A Dispersant Injection Pump | 17L073PM073A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:29/ O1011107:4A | TS-O-06:30/ O1011107:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -A | 17XYSPM073LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300003 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.23 | 17-MC-DCS-004 | TS-O-02 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073A Dispersant Injection Pump | 17L073PM073A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:24/ O1011205:26A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -A | 17XYSTM073LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor START command | 4124-FY-VD-BD17217L07300003 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.03 | 17-MC-DCS-004 | TS-P-03 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073A Dispersant Injection Pump | 17L073PM073A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:4/ O1011206:15A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -B | 17XSM073LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300003 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.16 | 17-MC-DCS-004 | TS-O-06 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073B Dispersant Injection Pump | PM073B НАСОС ДИСПЕРСАНТА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:31/ O1011107:5A | TS-O-06:32/ O1011107:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -B | 17XSAM073LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300003 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.17 | 17-MC-DCS-004 | TS-O-06 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073B Dispersant Injection Pump | 17L073PM073B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:33/ O1011107:6A | TS-O-06:34/ O1011107:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -B | 17XSRM073LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300003 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.18 | 17-MC-DCS-004 | TS-O-06 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073B Dispersant Injection Pump | 17L073PM073B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:35/ O1011107:7A | TS-O-06:36/ O1011107:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -B | 17XYSPM073LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300003 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.25 | 17-MC-DCS-004 | TS-O-02 | 25 | 26 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073B Dispersant Injection Pump | 17L073PM073B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:26/ O1011205:27A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -073LP -B | 17XYSTM073LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor START command | 4124-FY-VD-BD17217L07300003 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.05 | 17-MC-DCS-004 | TS-P-03 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-073B Dispersant Injection Pump | 17L073PM073B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:6/ O1011206:16A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -A | 17XSM074LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300004 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.19 | 17-MC-DCS-004 | TS-O-06 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074A Non-Oxidant Biocide Injection Pump | PM074A НАСОС НЕОКИСЛ. БИОЦИДОВ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:37/ O1011107:8A | TS-O-06:38/ O1011107:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -A | 17XSAM074LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300004 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.20 | 17-MC-DCS-004 | TS-O-06 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074A Non-Oxidant Biocide Injection Pump | 17L073PM074A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:39/ O1011107:9A | TS-O-06:40/ O1011107:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -A | 17XSRM074LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300004 | DCS_DI_03 | MCC |  | 17-I-DD-N-009BL02 | 24 Pair | Pr.21 | 17-MC-DCS-004 | TS-O-06 | 41 | 42 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074A Non-Oxidant Biocide Injection Pump | 17L073PM074A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:41/ O1011107:10A | TS-O-06:42/ O1011107:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -A | 17XYSPM074LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300004 | DCS_DO_03 | MCC |  | 17-I-CD-N-013BL02 | 30 Core | C.27 | 17-MC-DCS-004 | TS-O-02 | 27 | 28 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074A Non-Oxidant Biocide Injection Pump | 17L073PM074A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-02:28/ O1011205:28A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -A | 17XYSTM074LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17217L07300004 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.01 | 17-MC-DCS-004 | TS-O-03 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074A Non-Oxidant Biocide Injection Pump | 17L073PM074A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:2/ O1011205:29A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -B | 17XSM074LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300004 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.01 | 17-MC-DCS-004 | TS-R-01 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074B Non-Oxidant Biocide Injection Pump | PM074B НАСОС НЕОКИСЛ. БИОЦИДОВ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:1/ O1011107:11A | TS-R-01:2/ O1011107:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -B | 17XSAM074LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300004 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.02 | 17-MC-DCS-004 | TS-R-01 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074B Non-Oxidant Biocide Injection Pump | 17L073PM074B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:3/ O1011107:12A | TS-R-01:4/ O1011107:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -B | 17XSRM074LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300004 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.03 | 17-MC-DCS-004 | TS-R-01 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074B Non-Oxidant Biocide Injection Pump | 17L073PM074B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:5/ O1011107:13A | TS-R-01:6/ O1011107:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -B | 17XYSPM074LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300004 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.03 | 17-MC-DCS-004 | TS-O-03 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074B Non-Oxidant Biocide Injection Pump | 17L073PM074B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:4/ O1011205:30A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -074LP -B | 17XYSTM074LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17217L07300004 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.05 | 17-MC-DCS-004 | TS-O-03 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-074B Non-Oxidant Biocide Injection Pump | 17L073PM074B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:6/ O1011205:31A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -A | 17XSM075LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300005 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.04 | 17-MC-DCS-004 | TS-R-01 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075A Chlorine Enhancer Injection Pump | PM075A НАСОС УСИЛ ХЛОРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:7/ O1011107:14A | TS-R-01:8/ O1011107:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -A | 17XSAM075LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300005 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.05 | 17-MC-DCS-004 | TS-R-01 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075A Chlorine Enhancer Injection Pump | 17L073PM075A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:9/ O1011107:15A | TS-R-01:10/ O1011107:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -A | 17XSRM075LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300005 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.06 | 17-MC-DCS-004 | TS-R-01 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075A Chlorine Enhancer Injection Pump | 17L073PM075A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:11/ O1011107:16A | TS-R-01:12/ O1011107:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -A | 17XYSPM075LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300005 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.07 | 17-MC-DCS-004 | TS-O-03 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011205 | TUA711-DIO32 | 17-SC-DCS-002/O1011205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011205 | 6 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075A Chlorine Enhancer Injection Pump | 17L073PM075A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:8/ O1011205:32A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -A | 17XYSTM075LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17217L07300005 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.09 | 17-MC-DCS-004 | TS-O-03 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075A Chlorine Enhancer Injection Pump | 17L073PM075A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:10/ O1011206:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -B | 17XSM075LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300005 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.07 | 17-MC-DCS-004 | TS-R-01 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075B Chlorine Enhancer Injection Pump | PM075B НАСОС УСИЛ ХЛОРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:13/ O1011107:17A | TS-R-01:14/ O1011107:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -B | 17XSAM075LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300005 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.08 | 17-MC-DCS-004 | TS-R-01 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075B Chlorine Enhancer Injection Pump | 17L073PM075B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:15/ O1011107:18A | TS-R-01:16/ O1011107:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -B | 17XSRM075LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300005 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.09 | 17-MC-DCS-004 | TS-R-01 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075B Chlorine Enhancer Injection Pump | 17L073PM075B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:17/ O1011107:19A | TS-R-01:18/ O1011107:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -B | 17XYSPM075LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300005 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.11 | 17-MC-DCS-004 | TS-O-03 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075B Chlorine Enhancer Injection Pump | 17L073PM075B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:12/ O1011206:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -075LP -B | 17XYSTM075LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17217L07300005 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.13 | 17-MC-DCS-004 | TS-O-03 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-075B Chlorine Enhancer Injection Pump | 17L073PM075B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:14/ O1011206:3A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -A | 17XSM076LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.10 | 17-MC-DCS-004 | TS-R-01 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076A 12-14% Sodium Hypochlorite Inj. | PM076A ГИПОХЛОРИТ НАТРИЯ 15% | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:19/ O1011107:20A | TS-R-01:20/ O1011107:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -A | 17XSAM076LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.11 | 17-MC-DCS-004 | TS-R-01 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076A 12-14% Sodium Hypochlorite Inj. | 17L073PM076A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:21/ O1011107:21A | TS-R-01:22/ O1011107:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -A | 17XSRM076LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.12 | 17-MC-DCS-004 | TS-R-01 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076A 12-14% Sodium Hypochlorite Inj. | 17L073PM076A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:23/ O1011107:22A | TS-R-01:24/ O1011107:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -A | 17XYSPM076LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300006 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.15 | 17-MC-DCS-004 | TS-O-03 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076A 12-14% Sodium Hypochlorite Inj. | 17L073PM076A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:16/ O1011206:4A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -A | 17XYSTM076LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17217L07300006 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.17 | 17-MC-DCS-004 | TS-O-03 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076A 12-14% Sodium Hypochlorite Inj. | 17L073PM076A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:18/ O1011206:5A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -B | 17XSM076LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.13 | 17-MC-DCS-004 | TS-R-01 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076B 12-14% Sodium Hypochlorite Inj. | PM076B ГИПОХЛОРИТ НАТРИЯ 15% | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:25/ O1011107:23A | TS-R-01:26/ O1011107:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -B | 17XSAM076LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.14 | 17-MC-DCS-004 | TS-R-01 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076B 12-14% Sodium Hypochlorite Inj. | 17L073PM076B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:27/ O1011107:24A | TS-R-01:28/ O1011107:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -B | 17XSRM076LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.15 | 17-MC-DCS-004 | TS-R-01 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076B 12-14% Sodium Hypochlorite Inj. | 17L073PM076B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:29/ O1011107:25A | TS-R-01:30/ O1011107:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -B | 17XYSPM076LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-FY-VD-BD17217L07300006 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.19 | 17-MC-DCS-004 | TS-O-03 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076B 12-14% Sodium Hypochlorite Inj. | 17L073PM076B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:20/ O1011206:6A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -076LP -B | 17XYSTM076LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-FY-VD-BD17217L07300006 | DCS_DO_03 | MCC |  | 17-I-CD-N-014BL02 | 30 Core | C.21 | 17-MC-DCS-004 | TS-O-03 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-076B 12-14% Sodium Hypochlorite Inj. | 17L073PM076B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-03:22/ O1011206:7A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -077LP -A | 17XSAM077LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.16 | 17-MC-DCS-004 | TS-R-01 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-077A Na Hypochlorite Centrifugal Pump | 17L073PM077A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:31/ O1011107:26A | TS-R-01:32/ O1011107:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -077LP -A | 17XSM077LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.07 | 17-MC-DCS-004 | TS-R-05 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-077A Na Hypochlorite Centrifugal Pump | PM077LPA НАСОС ПЕРЕКАЧ. РЕАГЕНТ. | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:13/ O1011108:32A | TS-R-05:14/ O1011108:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -077LP -B | 17XSAM077LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.17 | 17-MC-DCS-004 | TS-R-01 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-077B Na Hypochlorite Centrifugal Pump | 17L073PM077B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:33/ O1011107:27A | TS-R-01:34/ O1011107:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -077LP -B | 17XSM077LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-FY-VD-BD17217L07300006 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.08 | 17-MC-DCS-004 | TS-R-05 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-L-073-PM-077B Na Hypochlorite Centrifugal Pump | PM077LPB НАСОС ПЕРЕКАЧ. РЕАГЕНТ. | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:15/ O1011109:1A | TS-R-05:16/ O1011109:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101 -BLK | 17XSM101BLK |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-FB-VD-BD00317L11111310 | DCS_DI_05 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.04 | 17-MC-DCS-005 | TS-G-04 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | ВЕНТИЛЯТОР КОТЛА 17-L-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:7/ O1010115:29A | TS-G-04:8/ O1010115:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101 -BLK | 17XSAM101BLK |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-FB-VD-BD00317L11111310 | DCS_DI_05 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.05 | 17-MC-DCS-005 | TS-G-04 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-L-111-KM-101-B ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:9/ O1010115:30A | TS-G-04:10/ O1010115:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101 -BLK | 17XSRM101BLK |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-FB-VD-BD00317L11111310 | DCS_DI_05 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.06 | 17-MC-DCS-005 | TS-G-04 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-L-111-KM-101-B МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:11/ O1010115:31A | TS-G-04:12/ O1010115:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101 -BLK | 17XYSPM101BLK |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-FB-VD-BD00317L11111310 | DCS_DO_04 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.05 | 17-MC-DCS-003 | TS-G-07 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-L-111-KM-101-B СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:6/ O1010214:7A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101 -BLK | 17XYSTM101BLK |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-FB-VD-BD00317L11111310 | DCS_DO_04 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.07 | 17-MC-DCS-003 | TS-G-07 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-L-111-KM-101-B ПУСК | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:8/ O1010214:8A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101K -A | 17XSM101KA |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_05 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.01 | 17-MC-DCS-005 | TS-F-04 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR MAIN MOTOR 17-KM-101A | ОСН ДВИГАТЕЛЬ КОМПРЕССОРА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:1/ O1010115:11A | TS-F-04:2/ O1010115:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101K -A | 17XSAM101KA |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_05 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.02 | 17-MC-DCS-005 | TS-F-04 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR MAIN MOTOR 17-KM-101A | 17-KM-101A ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:3/ O1010115:12A | TS-F-04:4/ O1010115:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101K -A | 17XSRM101KA |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_05 | MCC |  | 17-I-DD-N-019BL02 | 24 Pair | Pr.03 | 17-MC-DCS-005 | TS-F-04 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010115 | TUA711-DIO32 | 17-SC-DCS-001/O1010115/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010115 | 16 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR MAIN MOTOR 17-KM-101A | 17-KM-101A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:5/ O1010115:13A | TS-F-04:6/ O1010115:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101K -A | 17XYSPM101KA |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_04 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.01 | 17-MC-DCS-003 | TS-G-05 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR MAIN MOTOR 17-KM-101A | 17-KM-101A СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:2/ O1010213:19A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -101K -A | 17XYSTM101KA |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_04 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.03 | 17-MC-DCS-003 | TS-G-05 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR MAIN MOTOR 17-KM-101A | 17-KM-101A ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:4/ O1010213:20A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -102KP | 17XSM102KP |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GP-VD-BD17917K101004_SH.4 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.04 | 17-MC-DCS-003 | TS-F-05 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR 17-K-101-P-102 LO PUMP | 17K101P102 КОМПРЕССОР | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:7/ O1010207:28A | TS-F-05:8/ O1010207:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -102KP | 17XSAM102KP |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GP-VD-BD17917K101004_SH.4 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.05 | 17-MC-DCS-003 | TS-F-05 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR 17-K-101-P-102 LO PUMP | 17K101P102 ДОСТУПНО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:9/ O1010207:29A | TS-F-05:10/ O1010207:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -102KP | 17XSRM102KP |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GP-VD-BD17917K101004_SH.4 | DCS_DI_03 | MCC |  | 17-I-DD-N-005BL02 | 24 Pair | Pr.06 | 17-MC-DCS-003 | TS-F-05 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010207 | TUA711-DIO32 | 17-SC-DCS-001/O1010207/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010207 | 8 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR 17-K-101-P-102 LO PUMP | 17K101P102 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:11/ O1010207:30A | TS-F-05:12/ O1010207:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -102KP | 17XYSPM102KP |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GP-VD-BD17917K101004_SH.4 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.09 | 17-MC-DCS-003 | TS-G-05 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR 17-K-101-P-102 LO PUMP | 17K101P102 СТОП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:10/ O1010213:23A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -102KP | 17XYSTM102KP |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GP-VD-BD17917K101004_SH.4 | DCS_DO_03 | MCC |  | 17-I-CD-N-009BL02 | 30 Core | C.11 | 17-MC-DCS-003 | TS-G-05 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010213 | TUA711-DIO32 | 17-SC-DCS-001/O1010213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010213 | 14 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR 17-K-101-P-102 LO PUMP | 17K101P102 ПУСК | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-05:12/ O1010213:24A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -A | 17XSM111A |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы 26.06.24 по TQ-061 добавлен | Сигнал | Motor Running status | #N/A | DCS_DI_05 |  |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.20 | 17-MC-DCS-003 | TS-F-03 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111A Centrifugal Pumps | 17-P-111A НАСОС КПВ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | RUNNING | NOT RUNNING | [20 empty] | TS-F-03:39/ O1010208:19A | TS-F-03:40/ O1010208:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -A | 17XSAM111A |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы 26.06.24 по TQ-061 добавлен | Сигнал | Motor Available status | #N/A | DCS_DI_05 |  |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.21 | 17-MC-DCS-003 | TS-F-03 | 41 | 42 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111A Centrifugal Pumps | 17-P-111A ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | START | NO ACTION | [20 empty] | TS-F-03:41/ O1010208:20A | TS-F-03:42/ O1010208:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -A | 17XSRM111A |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы 26.06.24 по TQ-061 добавлен | Сигнал | Motor Remote status | #N/A | DCS_DI_05 |  |  | 17-I-DD-N-003BL02 | 24 Pair | Pr.22 | 17-MC-DCS-003 | TS-F-03 | 43 | 44 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111A Centrifugal Pumps | 17-P-111A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | NO ACTION | STOP | [20 empty] | TS-F-03:43/ O1010208:21A | TS-F-03:44/ O1010208:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -A | 17XYSPM111A |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы 26.06.24 по TQ-061 добавлен | Сигнал | Motor Stop command | #N/A | DCS_DO_04 |  |  | 17-I-CD-N-008BL02 | 30 Core | C.25 | 17-MC-DCS-003 | TS-G-04 | 25 | 26 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111A Centrifugal Pumps | 17-P-111A СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | AVAILABLE | NOT AVLB | [21 empty] | TS-G-04:26/ O1011213:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -A | 17XYSTM111A |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы 26.06.24 по TQ-061 добавлен | Сигнал | Motor Start command | #N/A | DCS_DO_04 |  |  | 17-I-CD-N-008BL02 | 30 Core | C.27 | 17-MC-DCS-003 | TS-G-04 | 27 | 28 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111A Centrifugal Pumps | 17-P-111A ПУСК | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | REMOTE | LOCAL | [21 empty] | TS-G-04:28/ O1011213:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -B | 17XSM111B |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Running status | 4124-XZ-DM-21711201 | DCS_DI_05 | MCC |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.06 | 17-MC-DCS-003 | TS-H-01 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111B Centrifugal Pumps | 17-P-111B НАСОС КПВ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:11/ O1010208:13A | TS-H-01:12/ O1010208:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -B | 17XSAM111B |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Available status | 4124-XZ-DM-21711201 | DCS_DI_05 | MCC |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.07 | 17-MC-DCS-003 | TS-H-01 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111B Centrifugal Pumps | 17-P-111B ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:13/ O1010208:14A | TS-H-01:14/ O1010208:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -B | 17XSRM111B |  | DI-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Remote status | 4124-XZ-DM-21711201 | DCS_DI_05 | MCC |  | 17-I-DD-N-007BL02 | 24 Pair | Pr.08 | 17-MC-DCS-003 | TS-H-01 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111B Centrifugal Pumps | 17-P-111B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:15/ O1010208:15A | TS-H-01:16/ O1010208:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -B | 17XYSPM111B |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Stop command | 4124-XZ-DM-21711201 | DCS_DO_04 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.25 | 17-MC-DCS-003 | TS-G-07 | 25 | 26 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111B Centrifugal Pumps | 17-P-111B СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:26/ O1010214:17A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.1 | 17-M -111 -B | 17XYSTM111B |  | DO-NIS (MCC 220VDC) DCS | 28.06.2024 замена типовой схемы | Сигнал | Motor Start command | 4124-XZ-DM-21711201 | DCS_DO_04 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.27 | 17-MC-DCS-003 | TS-G-07 | 27 | 28 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-111B Centrifugal Pumps | 17-P-111B ПУСК | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:28/ O1010214:18A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -111AL0 -01B | 17XYSPM111AL001B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.13 | 17-MC-DCS-003 | TS-G-07 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-STP-111A-PM-001B Auxiliary Oil Pump | 17-STP-111A-PM-001B СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:14/ O1010214:11A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -111AL0 -01B | 17XYSTM111AL001B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DO_03 | MCC |  | 17-I-CD-N-011BL02 | 30 Core | C.15 | 17-MC-DCS-003 | TS-G-07 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1010214 | TUA711-DIO32 | 17-SC-DCS-001/O1010214/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010214 | 15 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-STP-111A-PM-001B Auxiliary Oil Pump | M111B | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-G-07:16/ O1010214:12A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -111AL0 -01B | 17XSM111AL001B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running Status | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.10 | 17-MC-DCS-005 | TS-G-04 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-STP-111A-PM-001B Auxiliary Oil Pump | ВСПОМ. МАСЛЯНЫЙ НАСОС | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:19/ O1010300:3A | TS-G-04:20/ O1010300:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -111AL0 -01B | 17XSAM111AL001B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor available status | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.11 | 17-MC-DCS-005 | TS-G-04 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-STP-111A-PM-001B Auxiliary Oil Pump | 17-STP-111A-PM-001B ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:21/ O1010300:4A | TS-G-04:22/ O1010300:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -111AL0 -01B | 17XSRM111AL001B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Local/Remote status | 4124-GG-VD-BD17117P111037_SH.3 | DCS_DI_03 | MCC |  | 17-I-DD-N-020BL02 | 24 Pair | Pr.12 | 17-MC-DCS-005 | TS-G-04 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-STP-111A-PM-001B Auxiliary Oil Pump | 17-STP-111A-PM-001B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:23/ O1010300:5A | TS-G-04:24/ O1010300:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113500 | 17MXSA113500 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.01 | 17-MC-DCS-001 | TS-H-02 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113500 ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:1/ O1010202:1A | TS-H-02:2/ O1010202:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113500 | 17MXSR113500 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Local/Remote | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.02 | 17-MC-DCS-001 | TS-H-02 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113500 МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:3/ O1010202:2A | TS-H-02:4/ O1010202:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113500 | 17MZSH113500 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.03 | 17-MC-DCS-001 | TS-H-02 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113500 ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:5/ O1010202:3A | TS-H-02:6/ O1010202:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113500 | 17MZSL113500 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.04 | 17-MC-DCS-001 | TS-H-02 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113500 ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:7/ O1010202:4A | TS-H-02:8/ O1010202:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113500 | 17MXYSP113500 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DO_01 | Field |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | C.01 | 17-MC-DCS-001 | TS-G-07 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 19 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113500 СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-07:1/ O1010211:19A | TS-G-07:2/ O1010211:19C | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113500 | 17MXYH113500 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DO_01 | Field |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | C.03 | 17-MC-DCS-001 | TS-G-07 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 20 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113500 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-07:3/ O1010211:20A | TS-G-07:4/ O1010211:20C | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113500 | 17MXYL113500 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DO_01 | Field |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | C.05 | 17-MC-DCS-001 | TS-G-07 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 21 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113500 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-07:5/ O1010211:21A | TS-G-07:6/ O1010211:21C | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113501 | 17MZT113501 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | MOV Position Signal | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.01 | 17-MC-DCS-008 | TS-P-04 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010009_U10 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113501 ПОЛОЖЕНИЕ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100.0 | % | [5 empty] | TS-P-04:1/ O1010009_U10:3 | TS-P-04:2/ O1010009_U10:4 |  |  | O1010009:10A/ O1010009_U10:5 | O1010009:10C/ O1010009_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113501 | 17MY113501 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | MOV Inching Command | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.02 | 17-MC-DCS-008 | TS-P-04 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010108R_U10 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 10 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113501 МЕДЛЕННО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-P-04:3/ O1010108R_U10:3 | TS-P-04:4/ O1010108R_U10:4 |  |  | O1010108R:10A/ O1010108R_U10:5 | O1010108R:10C/ O1010108R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113501 | 17MXSA113501 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.13 | 17-MC-DCS-001 | TS-H-02 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113501 ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:25/ O1010201:22A | TS-H-02:26/ O1010201:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113501 | 17MXSR113501 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Local/Remote | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.14 | 17-MC-DCS-001 | TS-H-02 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113501 МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:27/ O1010201:23A | TS-H-02:28/ O1010201:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113501 | 17MZSH113501 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.15 | 17-MC-DCS-001 | TS-H-02 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113501 ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:29/ O1010201:24A | TS-H-02:30/ O1010201:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113501 | 17MZSL113501 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.16 | 17-MC-DCS-001 | TS-H-02 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | 17-MOV-113501 ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:31/ O1010201:25A | TS-H-02:32/ O1010201:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113502 | 17MXSA113502 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.05 | 17-MC-DCS-001 | TS-H-02 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SILENCER 17-L-111-SL-103 | 17-MOV-113502 ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:9/ O1010202:5A | TS-H-02:10/ O1010202:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113502 | 17MXSR113502 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Local/Remote | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.06 | 17-MC-DCS-001 | TS-H-02 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SILENCER 17-L-111-SL-103 | 17-MOV-113502 МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:11/ O1010202:6A | TS-H-02:12/ O1010202:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113502 | 17MZSH113502 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.07 | 17-MC-DCS-001 | TS-H-02 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SILENCER 17-L-111-SL-103 | 17-MOV-113502 ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:13/ O1010202:7A | TS-H-02:14/ O1010202:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113502 | 17MZSL113502 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.08 | 17-MC-DCS-001 | TS-H-02 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SILENCER 17-L-111-SL-103 | 17-MOV-113502 ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:15/ O1010202:8A | TS-H-02:16/ O1010202:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113502 | 17MXYSP113502 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DO_01 | Field |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | C.07 | 17-MC-DCS-001 | TS-G-07 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 22 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | SILENCER 17-L-111-SL-103 | 17-MOV-113502 СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-07:7/ O1010211:22A | TS-G-07:8/ O1010211:22C | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113502 | 17MXYH113502 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DO_01 | Field |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | C.09 | 17-MC-DCS-001 | TS-G-07 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 23 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | SILENCER 17-L-111-SL-103 | 17-MOV-113502 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-07:9/ O1010211:23A | TS-G-07:10/ O1010211:23C | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113502 | 17MXYL113502 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_DO_01 | Field |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | C.11 | 17-MC-DCS-001 | TS-G-07 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 24 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | SILENCER 17-L-111-SL-103 | 17-MOV-113502 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-07:11/ O1010211:24A | TS-G-07:12/ O1010211:24C | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113503 | 17MZSL113503 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.12 | 17-MC-DCS-001 | TS-H-02 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Intermittent blow down from 17-L-111 | 17-MOV-113503 ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:23/ O1010201:21A | TS-H-02:24/ O1010201:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113503 | 17MXSA113503 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.09 | 17-MC-DCS-001 | TS-H-02 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Intermittent blow down from 17-L-111 | 17-MOV-113503 ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:17/ O1010202:9A | TS-H-02:18/ O1010202:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113503 | 17MXSR113503 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.10 | 17-MC-DCS-001 | TS-H-02 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Intermittent blow down from 17-L-111 | 17-MOV-113503 МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:19/ O1010202:10A | TS-H-02:20/ O1010202:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113503 | 17MZSH113503 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_DI_01 | Field |  | 17-C-DD-N-002FL11-L111 | 24 Pair | Pr.11 | 17-MC-DCS-001 | TS-H-02 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Intermittent blow down from 17-L-111 | 17-MOV-113503 ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-02:21/ O1010202:11A | TS-H-02:22/ O1010202:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113503 | 17MXYSP113503 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_DO_01 | Field |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | C.13 | 17-MC-DCS-001 | TS-G-07 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 25 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Intermittent blow down from 17-L-111 | 17-MOV-113503 СТОП | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-07:13/ O1010211:25A | TS-G-07:14/ O1010211:25C | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113503 | 17MXYH113503 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_DO_01 | Field |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | C.15 | 17-MC-DCS-001 | TS-G-07 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 26 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Intermittent blow down from 17-L-111 | 17-MOV-113503 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-07:15/ O1010211:26A | TS-G-07:16/ O1010211:26C | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113503 | 17MXYL113503 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_DO_01 | Field |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | C.17 | 17-MC-DCS-001 | TS-G-07 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 27 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Intermittent blow down from 17-L-111 | 17-MOV-113503 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-G-07:17/ O1010211:27A | TS-G-07:18/ O1010211:27C | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -A | 17MZT113521A |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | MOV Position Signal | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.03 | 17-MC-DCS-008 | TS-P-04 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010009_U11 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113521 -A ПОЛОЖЕНИЕ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100.0 | % | [5 empty] | TS-P-04:5/ O1010009_U11:3 | TS-P-04:6/ O1010009_U11:4 |  |  | O1010009:11A/ O1010009_U11:5 | O1010009:11C/ O1010009_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -A | 17MY113521A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | MOV Inching Command | 4124-FB-VD-BD00317L11111303 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.04 | 17-MC-DCS-008 | TS-P-04 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010108R_U11 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 11 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113521 -A МЕДЛЕННО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-P-04:7/ O1010108R_U11:3 | TS-P-04:8/ O1010108R_U11:4 |  |  | O1010108R:11A/ O1010108R_U11:5 | O1010108R:11C/ O1010108R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -A | 17MXSA113521A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.01 | 17-MC-DCS-001 | TS-H-01 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113521 -A ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:1/ O1010201:26A | TS-H-01:2/ O1010201:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -A | 17MXSR113521A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Local/Remote | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.02 | 17-MC-DCS-001 | TS-H-01 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010201 | TUA711-DIR32 | 17-SC-DCS-001/O1010201/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010201 | 2 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113521 -A МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:3/ O1010201:27A | TS-H-01:4/ O1010201:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -A | 17MZSH113521A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.03 | 17-MC-DCS-001 | TS-H-01 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113521 -A ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:5/ O1010202:12A | TS-H-01:6/ O1010202:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -A | 17MZSL113521A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.04 | 17-MC-DCS-001 | TS-H-01 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113521 -A ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:7/ O1010202:13A | TS-H-01:8/ O1010202:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -B | 17MZT113521B |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | MOV Position Signal | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.05 | 17-MC-DCS-008 | TS-P-04 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010009_U12 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113521 -B ПОЛОЖЕНИЕ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100.0 | % | [5 empty] | TS-P-04:9/ O1010009_U12:3 | TS-P-04:10/ O1010009_U12:4 |  |  | O1010009:12A/ O1010009_U12:5 | O1010009:12C/ O1010009_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -B | 17MY113521B |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | MOV Inching Command | 4124-FB-VD-BD00317L11111303 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.06 | 17-MC-DCS-008 | TS-P-04 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010108R_U12 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 12 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113521 -B МЕДЛЕННО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-P-04:11/ O1010108R_U12:3 | TS-P-04:12/ O1010108R_U12:4 |  |  | O1010108R:12A/ O1010108R_U12:5 | O1010108R:12C/ O1010108R_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -B | 17MXSA113521B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.05 | 17-MC-DCS-001 | TS-H-01 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113521 -B ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:9/ O1010202:14A | TS-H-01:10/ O1010202:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -B | 17MXSR113521B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Local/Remote | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.06 | 17-MC-DCS-001 | TS-H-01 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113521 -B МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:11/ O1010202:15A | TS-H-01:12/ O1010202:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -B | 17MZSH113521B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.07 | 17-MC-DCS-001 | TS-H-01 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113521 -B ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:13/ O1010202:16A | TS-H-01:14/ O1010202:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113521 -B | 17MZSL113521B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.08 | 17-MC-DCS-001 | TS-H-01 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113521 -B ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:15/ O1010202:17A | TS-H-01:16/ O1010202:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -A | 17MZT113522A |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | MOV Position Signal | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.07 | 17-MC-DCS-008 | TS-P-04 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010009_U13 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113522 -A ПОЛОЖЕНИЕ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100.0 | % | [5 empty] | TS-P-04:13/ O1010009_U13:3 | TS-P-04:14/ O1010009_U13:4 |  |  | O1010009:13A/ O1010009_U13:5 | O1010009:13C/ O1010009_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -A | 17MY113522A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | MOV Inching Command | 4124-FB-VD-BD00317L11111303 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.08 | 17-MC-DCS-008 | TS-P-04 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010108R_U13 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 13 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113522 -A МЕДЛЕННО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-P-04:15/ O1010108R_U13:3 | TS-P-04:16/ O1010108R_U13:4 |  |  | O1010108R:13A/ O1010108R_U13:5 | O1010108R:13C/ O1010108R_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -A | 17MXSA113522A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.09 | 17-MC-DCS-001 | TS-H-01 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113522 -A ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:17/ O1010202:18A | TS-H-01:18/ O1010202:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -A | 17MXSR113522A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Local/Remote | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.10 | 17-MC-DCS-001 | TS-H-01 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113522 -A МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:19/ O1010202:19A | TS-H-01:20/ O1010202:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -A | 17MZSH113522A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.11 | 17-MC-DCS-001 | TS-H-01 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113522 -A ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:21/ O1010202:20A | TS-H-01:22/ O1010202:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -A | 17MZSL113522A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.12 | 17-MC-DCS-001 | TS-H-01 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE 17-L-111-STK-101-A | 17-MOV-113522 -A ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:23/ O1010202:21A | TS-H-01:24/ O1010202:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -B | 17MZT113522B |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | MOV Position Signal | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.09 | 17-MC-DCS-008 | TS-P-04 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010009_U14 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113522 -B ПОЛОЖЕНИЕ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100.0 | % | [5 empty] | TS-P-04:17/ O1010009_U14:3 | TS-P-04:18/ O1010009_U14:4 |  |  | O1010009:14A/ O1010009_U14:5 | O1010009:14C/ O1010009_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -B | 17MY113522B |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | MOV Inching Command | 4124-FB-VD-BD00317L11111303 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL11-L111 | 12 Pair | Pr.10 | 17-MC-DCS-008 | TS-P-04 | 19 | 20 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010108R_U14 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 14 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113522 -B МЕДЛЕННО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [5 empty] | TS-P-04:19/ O1010108R_U14:3 | TS-P-04:20/ O1010108R_U14:4 |  |  | O1010108R:14A/ O1010108R_U14:5 | O1010108R:14C/ O1010108R_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -B | 17MXSA113522B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.13 | 17-MC-DCS-001 | TS-H-01 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113522 -B ДОСТУПНО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:25/ O1010202:22A | TS-H-01:26/ O1010202:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -B | 17MXSR113522B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Local/Remote | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.14 | 17-MC-DCS-001 | TS-H-01 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113522 -B МЕСТН/ДИСТАНЦ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:27/ O1010202:23A | TS-H-01:28/ O1010202:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -B | 17MZSH113522B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.15 | 17-MC-DCS-001 | TS-H-01 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113522 -B ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:29/ O1010202:24A | TS-H-01:30/ O1010202:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113522 -B | 17MZSL113522B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DD-N-003FL11-L111 | 24 Pair | Pr.16 | 17-MC-DCS-001 | TS-H-01 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FAN MOTOR 17-L-111-KM-101-B | 17-MOV-113522 -B ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-01:31/ O1010202:25A | TS-H-01:32/ O1010202:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113531 -A | 17MZSH113531A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DB-N-001FL11-L111 | 24 Pair | Pr.01 | 17-MC-DCS-001 | TS-F-01 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STACK DAMPER 17-L111-X-101 | 17-L111-X-101 ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-01:1/ O1010200:1A | TS-F-01:2/ O1010200:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113531 -A | 17MZSL113531A |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DB-N-001FL11-L111 | 24 Pair | Pr.03 | 17-MC-DCS-001 | TS-F-01 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STACK DAMPER 17-L111-X-101 | 17-L111-X-101 ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-01:5/ O1010200:3A | TS-F-01:6/ O1010200:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113531 -B | 17MZSH113531B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DB-N-001FL11-L111 | 24 Pair | Pr.02 | 17-MC-DCS-001 | TS-F-01 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STACK DAMPER 17-L111-X-101 | 17-L111-X-101 ОТКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-01:3/ O1010200:2A | TS-F-01:4/ O1010200:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -113531 -B | 17MZSL113531B |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed | 4124-FB-VD-BD00317L11111303 | DCS_DI_01 | Field |  | 17-C-DB-N-001FL11-L111 | 24 Pair | Pr.04 | 17-MC-DCS-001 | TS-F-01 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STACK DAMPER 17-L111-X-101 | 17-L111-X-101 ЗАКРЫТО | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-F-01:7/ O1010200:4A | TS-F-01:8/ O1010200:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -A | 17XSM131A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P131151 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.15 | 17-MC-DCS-005 | TS-G-01 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131A | P131A НАСОС ДУШЕЙ САМОПОМОЩИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:29/ O1011112:2A | TS-G-01:30/ O1011112:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -A | 17XSAM131A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P131151 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.16 | 17-MC-DCS-005 | TS-G-01 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131A | 17-P-131A ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:31/ O1011112:3A | TS-G-01:32/ O1011112:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -A | 17XSRM131A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P131151 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.17 | 17-MC-DCS-005 | TS-G-01 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131A | 17-P-131A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:33/ O1011112:4A | TS-G-01:34/ O1011112:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -A | 17XYSPM131A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P131151 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.09 | 17-MC-DCS-004 | TS-P-01 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131A | 17-P-131A ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:10/ O1011207:19A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -A | 17XYSTM131A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P131151 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.11 | 17-MC-DCS-004 | TS-P-01 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131A | 17-P-131A ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:12/ O1011207:20A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -B | 17XSM131B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-GG-VD-BD17217P131151 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.18 | 17-MC-DCS-005 | TS-G-01 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131B | P131B НАСОС ДУШЕЙ САМОПОМОЩИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:35/ O1011112:5A | TS-G-01:36/ O1011112:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -B | 17XSAM131B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-GG-VD-BD17217P131151 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.19 | 17-MC-DCS-005 | TS-G-01 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131B | 17-P-131B ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:37/ O1011112:6A | TS-G-01:38/ O1011112:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -B | 17XSRM131B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-GG-VD-BD17217P131151 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.20 | 17-MC-DCS-005 | TS-G-01 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131B | 17-P-131B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:39/ O1011112:7A | TS-G-01:40/ O1011112:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -B | 17XYSPM131B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-GG-VD-BD17217P131151 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.13 | 17-MC-DCS-004 | TS-P-01 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131B | 17-P-131B ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:14/ O1011207:21A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -B | 17XYSTM131B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-GG-VD-BD17217P131151 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.15 | 17-MC-DCS-004 | TS-P-01 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131B | 17-P-131B ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:16/ O1011207:22A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -C | 17XSM131C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21713001 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.21 | 17-MC-DCS-005 | TS-G-01 | 41 | 42 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131C | P131C НАСОС ДУШЕЙ САМОПОМОЩИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:41/ O1011112:8A | TS-G-01:42/ O1011112:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -C | 17XSAM131C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21713001 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.22 | 17-MC-DCS-005 | TS-G-01 | 43 | 44 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131C | 17-P-131C ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:43/ O1011112:9A | TS-G-01:44/ O1011112:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -C | 17XSRM131C |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21713001 | DCS_DI_03 | MCC |  | 17-I-DD-N-001BL02 | 24 Pair | Pr.23 | 17-MC-DCS-005 | TS-G-01 | 45 | 46 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131C | 17-P-131C МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-01:45/ O1011112:10A | TS-G-01:46/ O1011112:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -C | 17XYSPM131C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21713001 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.17 | 17-MC-DCS-004 | TS-P-01 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131C | 17-P-131C ОСТАНОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:18/ O1011207:23A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -131 -C | 17XYSTM131C |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21713001 | DCS_DO_03 | MCC |  | 17-I-CD-N-004BL02 | 30 Core | C.19 | 17-MC-DCS-004 | TS-P-01 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131C | 17-P-131C ПУСК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-01:20/ O1011207:24A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -A | 17TSHM140LPA |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714003 | DCS_DI_02 | Field |  | 17-J-DD-N-001FL11 | 06 Pair | Pr.02 | 17-MC-DCS-002 | TS-P-06 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011100_U9 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPA | 17-P-140LPA ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-06:3/ O1011100_U9:3 | TS-P-06:4/ O1011100_U9:4 |  |  | O1011100:9A/ O1011100_U9:5 | O1011100:9B/ O1011100_U9:6 | [6 empty] | 9A | 9B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -A | 17XSLM140LPA |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714003 | DCS_DI_04 | Field |  | 17-J-DD-N-001FL11 | 06 Pair | Pr.01 | 17-MC-DCS-002 | TS-P-06 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011100_U25 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPA | 17-P-140LPA УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-06:1/ O1011100_U25:3 | TS-P-06:2/ O1011100_U25:1 |  |  | O1011100:25A/ O1011100_U25:7 | O1011100:25B/ O1011100_U25:8 | [6 empty] | 25A | 25B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -A | 17XSM140LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.10 | 17-MC-DCS-004 | TS-R-05 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPA | P140LPA НАСОС КНС 1 ЛИВНЕВЫЙ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:19/ O1011109:3A | TS-R-05:20/ O1011109:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -A | 17XSAM140LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.11 | 17-MC-DCS-004 | TS-R-05 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPA | 17-P-140LPA ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:21/ O1011109:4A | TS-R-05:22/ O1011109:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -A | 17XSRM140LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.12 | 17-MC-DCS-004 | TS-R-05 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPA | 17-P-140LPA МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:23/ O1011109:5A | TS-R-05:24/ O1011109:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -A | 17XYSPM140LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.09 | 17-MC-DCS-004 | TS-P-04 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPA | 17-P-140LPA СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:10/ O1011206:31A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -A | 17XYSTM140LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.11 | 17-MC-DCS-004 | TS-P-04 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPA | 17-P-140LPA ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:12/ O1011206:32A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -B | 17TSHM140LPB |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714003 | DCS_DI_02 | Field |  | 17-J-DD-N-001FL11 | 06 Pair | Pr.04 | 17-MC-DCS-002 | TS-P-06 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011100_U10 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPB | 17-P-140LPB ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-06:7/ O1011100_U10:3 | TS-P-06:8/ O1011100_U10:4 |  |  | O1011100:10A/ O1011100_U10:5 | O1011100:10B/ O1011100_U10:6 | [6 empty] | 10A | 10B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -B | 17XSLM140LPB |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714003 | DCS_DI_04 | Field |  | 17-J-DD-N-001FL11 | 06 Pair | Pr.03 | 17-MC-DCS-002 | TS-P-06 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011100_U26 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPB | 17-P-140LPB УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-06:5/ O1011100_U26:3 | TS-P-06:6/ O1011100_U26:1 |  |  | O1011100:26A/ O1011100_U26:7 | O1011100:26B/ O1011100_U26:8 | [6 empty] | 26A | 26B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -B | 17XSM140LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.13 | 17-MC-DCS-004 | TS-R-05 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPB | P140LPB НАСОС КНС 1 ЛИВНЕВЫЙ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:25/ O1011109:6A | TS-R-05:26/ O1011109:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -B | 17XSAM140LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.14 | 17-MC-DCS-004 | TS-R-05 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPB | 17-P-140LPB ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:27/ O1011109:7A | TS-R-05:28/ O1011109:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -B | 17XSRM140LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.15 | 17-MC-DCS-004 | TS-R-05 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPB | 17-P-140LPB МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:29/ O1011109:8A | TS-R-05:30/ O1011109:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -B | 17XYSPM140LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.13 | 17-MC-DCS-004 | TS-P-04 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 1 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPB | 17-P-140LPB СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:14/ O1011207:1A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -140LP -B | 17XYSTM140LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.15 | 17-MC-DCS-004 | TS-P-04 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 2 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 1 pump 17-P-140LPB | 17-P-140LPB ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:16/ O1011207:2A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -A | 17TSHM141A |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714001 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.01 | 17-MC-DCS-002 | TS-O-08 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U1 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141A | 17-P-141A ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:1/ O1011100_U1:3 | TS-O-08:2/ O1011100_U1:4 |  |  | O1011100:1A/ O1011100_U1:5 | O1011100:1B/ O1011100_U1:6 | [6 empty] | 1A | 1B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -A | 17XSLM141A |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714001 | DCS_DI_04 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.09 | 17-MC-DCS-002 | TS-O-08 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U17 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141A | 17-P-141A УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:17/ O1011100_U17:3 | TS-O-08:18/ O1011100_U17:1 |  |  | O1011100:17A/ O1011100_U17:7 | O1011100:17B/ O1011100_U17:8 | [6 empty] | 17A | 17B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -A | 17XSM141A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.18 | 17-MC-DCS-004 | TS-R-01 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141A | P141A НАСОС ЛИВНЕВЫХ ВОД | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:35/ O1011107:28A | TS-R-01:36/ O1011107:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -A | 17XSAM141A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.19 | 17-MC-DCS-004 | TS-R-01 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141A | 17-P-141A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:37/ O1011107:29A | TS-R-01:38/ O1011107:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -A | 17XSRM141A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-010BL02 | 24 Pair | Pr.20 | 17-MC-DCS-004 | TS-R-01 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141A | 17-P-141A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-01:39/ O1011107:30A | TS-R-01:40/ O1011107:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -A | 17XYSPM141A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714001 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.07 | 17-MC-DCS-004 | TS-P-03 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141A | 17-P-141A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:8/ O1011206:17A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -A | 17XYSTM141A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714001 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.09 | 17-MC-DCS-004 | TS-P-03 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141A | 17-P-141A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:10/ O1011206:18A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -B | 17TSHM141B |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714001 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.02 | 17-MC-DCS-002 | TS-O-08 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U2 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141B | 17-P-141B ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:3/ O1011100_U2:3 | TS-O-08:4/ O1011100_U2:4 |  |  | O1011100:2A/ O1011100_U2:5 | O1011100:2B/ O1011100_U2:6 | [6 empty] | 2A | 2B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -B | 17XSLM141B |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714001 | DCS_DI_04 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.10 | 17-MC-DCS-002 | TS-O-08 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U18 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141B | 17-P-141B УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:19/ O1011100_U18:3 | TS-O-08:20/ O1011100_U18:1 |  |  | O1011100:18A/ O1011100_U18:7 | O1011100:18B/ O1011100_U18:8 | [6 empty] | 18A | 18B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -B | 17XSM141B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.01 | 17-MC-DCS-004 | TS-R-02 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141B | P141B НАСОС ЛИВНЕВЫХ ВОД | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:1/ O1011107:31A | TS-R-02:2/ O1011107:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -B | 17XSAM141B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.02 | 17-MC-DCS-004 | TS-R-02 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011107 | TUA711-DIO32 | 17-SC-DCS-002/O1011107/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011107 | 8 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141B | 17-P-141B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:3/ O1011107:32A | TS-R-02:4/ O1011107:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -B | 17XSRM141B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.03 | 17-MC-DCS-004 | TS-R-02 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141B | 17-P-141B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:5/ O1011108:1A | TS-R-02:6/ O1011108:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -B | 17XYSPM141B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714001 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.11 | 17-MC-DCS-004 | TS-P-03 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141B | 17-P-141B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:12/ O1011206:19A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -141 -B | 17XYSTM141B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714001 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.13 | 17-MC-DCS-004 | TS-P-03 | 13 | 14 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-141B | 17-P-141B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:14/ O1011206:20A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -A | 17TSHM142A |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714001 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.03 | 17-MC-DCS-002 | TS-O-08 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U3 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142A | 17-P-142A ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:5/ O1011100_U3:3 | TS-O-08:6/ O1011100_U3:4 |  |  | O1011100:3A/ O1011100_U3:5 | O1011100:3B/ O1011100_U3:6 | [6 empty] | 3A | 3B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -A | 17XSLM142A |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714001 | DCS_DI_04 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.11 | 17-MC-DCS-002 | TS-O-08 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U19 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142A | 17-P-142A УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:21/ O1011100_U19:3 | TS-O-08:22/ O1011100_U19:1 |  |  | O1011100:19A/ O1011100_U19:7 | O1011100:19B/ O1011100_U19:8 | [6 empty] | 19A | 19B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -A | 17XSM142A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.04 | 17-MC-DCS-004 | TS-R-02 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142A | P142A НАСОС ЗАГРЯЗНЕННОЙ ВОДЫ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:7/ O1011108:2A | TS-R-02:8/ O1011108:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -A | 17XSAM142A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.05 | 17-MC-DCS-004 | TS-R-02 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142A | 17-P-142A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:9/ O1011108:3A | TS-R-02:10/ O1011108:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -A | 17XYSPM142A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714001 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.15 | 17-MC-DCS-004 | TS-P-03 | 15 | 16 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142A | 17-P-142A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:16/ O1011206:21A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -B | 17TSHM142B |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714001 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.04 | 17-MC-DCS-002 | TS-O-08 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U4 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142A | 17-P-142B ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:7/ O1011100_U4:3 | TS-O-08:8/ O1011100_U4:4 |  |  | O1011100:4A/ O1011100_U4:5 | O1011100:4B/ O1011100_U4:6 | [6 empty] | 4A | 4B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -B | 17XSLM142B |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714001 | DCS_DI_04 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.12 | 17-MC-DCS-002 | TS-O-08 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U20 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142A | 17-P-142B УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:23/ O1011100_U20:3 | TS-O-08:24/ O1011100_U20:1 |  |  | O1011100:20A/ O1011100_U20:7 | O1011100:20B/ O1011100_U20:8 | [6 empty] | 20A | 20B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -B | 17XSM142B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.06 | 17-MC-DCS-004 | TS-R-02 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142B | P142B НАСОС ЗАГРЯЗНЕННОЙ ВОДЫ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:11/ O1011108:4A | TS-R-02:12/ O1011108:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -B | 17XSAM142B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714001 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.07 | 17-MC-DCS-004 | TS-R-02 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142B | 17-P-142B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:13/ O1011108:5A | TS-R-02:14/ O1011108:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -142 -B | 17XYSPM142B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714001 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.17 | 17-MC-DCS-004 | TS-P-03 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Contaminated Water Pump 17-P-142B | 17-P-142B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:18/ O1011206:22A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -A | 17TSHM143LPA |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714003 | DCS_DI_02 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.02 | 17-MC-DCS-002 | TS-Q-13 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U11 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPA | 17-P-143LPA ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:3/ O1011100_U11:3 | TS-Q-13:4/ O1011100_U11:4 |  |  | O1011100:11A/ O1011100_U11:5 | O1011100:11B/ O1011100_U11:6 | [6 empty] | 11A | 11B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -A | 17XSLM143LPA |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714003 | DCS_DI_04 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-13 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U27 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPA | 17-P-143LPA УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:1/ O1011100_U27:3 | TS-Q-13:2/ O1011100_U27:1 |  |  | O1011100:27A/ O1011100_U27:7 | O1011100:27B/ O1011100_U27:8 | [6 empty] | 27A | 27B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -A | 17XSM143LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.16 | 17-MC-DCS-004 | TS-R-05 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPA | P143LPA НАСОС КНС 2 ЛИВНЕВЫЙ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:31/ O1011109:9A | TS-R-05:32/ O1011109:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -A | 17XSAM143LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.17 | 17-MC-DCS-004 | TS-R-05 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPA | 17-P-143LPA ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:33/ O1011109:10A | TS-R-05:34/ O1011109:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -A | 17XSRM143LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.18 | 17-MC-DCS-004 | TS-R-05 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPA | 17-P-143LPA МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:35/ O1011109:11A | TS-R-05:36/ O1011109:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -A | 17XYSPM143LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.17 | 17-MC-DCS-004 | TS-P-04 | 17 | 18 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPA | 17-P-143LPA СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:18/ O1011207:3A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -A | 17XYSTM143LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.19 | 17-MC-DCS-004 | TS-P-04 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPA | 17-P-143LPA ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:20/ O1011207:4A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -B | 17TSHM143LPB |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714003 | DCS_DI_02 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.08 | 17-MC-DCS-002 | TS-Q-13 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U14 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPB | 17-P-143LPB ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:15/ O1011100_U14:3 | TS-Q-13:16/ O1011100_U14:4 |  |  | O1011100:14A/ O1011100_U14:5 | O1011100:14B/ O1011100_U14:6 | [6 empty] | 14A | 14B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -B | 17XSLM143LPB |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714003 | DCS_DI_04 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.07 | 17-MC-DCS-002 | TS-Q-13 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U30 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPB | 17-P-143LPB УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:13/ O1011100_U30:3 | TS-Q-13:14/ O1011100_U30:1 |  |  | O1011100:30A/ O1011100_U30:7 | O1011100:30B/ O1011100_U30:8 | [6 empty] | 30A | 30B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -B | 17XSM143LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.19 | 17-MC-DCS-004 | TS-R-05 | 37 | 38 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPB | P143LPB НАСОС КНС 2 ЛИВНЕВЫЙ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:37/ O1011109:12A | TS-R-05:38/ O1011109:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -B | 17XSAM143LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.20 | 17-MC-DCS-004 | TS-R-05 | 39 | 40 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPB | 17-P-143LPB ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:39/ O1011109:13A | TS-R-05:40/ O1011109:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -B | 17XSRM143LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.21 | 17-MC-DCS-004 | TS-R-05 | 41 | 42 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPB | 17-P-143LPB МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:41/ O1011109:14A | TS-R-05:42/ O1011109:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -B | 17XYSPM143LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.21 | 17-MC-DCS-004 | TS-P-04 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPB | 17-P-143LPB СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:22/ O1011207:5A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -143LP -B | 17XYSTM143LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.23 | 17-MC-DCS-004 | TS-P-04 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Water lift station 2 pump 17-P-143LPB | 17-P-143LPB ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:24/ O1011207:6A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -A | 17TSHM144A |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714002 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.05 | 17-MC-DCS-002 | TS-O-08 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U5 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-144A | 17-P-144A ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:9/ O1011100_U5:3 | TS-O-08:10/ O1011100_U5:4 |  |  | O1011100:5A/ O1011100_U5:5 | O1011100:5B/ O1011100_U5:6 | [6 empty] | 5A | 5B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -A | 17XSLM144A |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714002 | DCS_DI_04 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.13 | 17-MC-DCS-002 | TS-O-08 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U21 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-144A | 17-P-144A УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:25/ O1011100_U21:3 | TS-O-08:26/ O1011100_U21:1 |  |  | O1011100:21A/ O1011100_U21:7 | O1011100:21B/ O1011100_U21:8 | [6 empty] | 21A | 21B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -A | 17XSM144A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.08 | 17-MC-DCS-004 | TS-R-02 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144A | P144A НАСОС СБОРНИКА ЛИВН ВОД | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:15/ O1011108:6A | TS-R-02:16/ O1011108:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -A | 17XSRM144A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.09 | 17-MC-DCS-004 | TS-R-02 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144A | 17-P-144A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:17/ O1011108:7A | TS-R-02:18/ O1011108:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -A | 17XSAM144A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-021BL02 | 24 Pair | Pr.09 | 17-MC-DCS-004 | TS-R-05 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144A | 17-P-144A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-05:17/ O1011109:2A | TS-R-05:18/ O1011109:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -A | 17XYSPM144A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714002 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.19 | 17-MC-DCS-004 | TS-P-03 | 19 | 20 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144A | 17-P-144A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:20/ O1011206:23A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -A | 17XYSTM144A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714002 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.21 | 17-MC-DCS-004 | TS-P-03 | 21 | 22 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144A | 17-P-144A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:22/ O1011206:24A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -B | 17TSHM144B |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714002 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.06 | 17-MC-DCS-002 | TS-O-08 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U6 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-144B | 17-P-144B ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:11/ O1011100_U6:3 | TS-O-08:12/ O1011100_U6:4 |  |  | O1011100:6A/ O1011100_U6:5 | O1011100:6B/ O1011100_U6:6 | [6 empty] | 6A | 6B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -B | 17XSLM144B |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714002 | DCS_DI_04 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.14 | 17-MC-DCS-002 | TS-O-08 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U22 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-144B | 17-P-144B УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:27/ O1011100_U22:3 | TS-O-08:28/ O1011100_U22:1 |  |  | O1011100:22A/ O1011100_U22:7 | O1011100:22B/ O1011100_U22:8 | [6 empty] | 22A | 22B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -B | 17XSM144B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.10 | 17-MC-DCS-004 | TS-R-02 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144B | P144B НАСОС СБОРНИКА ЛИВН ВОД | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:19/ O1011108:8A | TS-R-02:20/ O1011108:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -B | 17XSAM144B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.11 | 17-MC-DCS-004 | TS-R-02 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144B | 17-P-144B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:21/ O1011108:9A | TS-R-02:22/ O1011108:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -B | 17XSRM144B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.12 | 17-MC-DCS-004 | TS-R-02 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144B | 17-P-144B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:23/ O1011108:10A | TS-R-02:24/ O1011108:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -B | 17XYSPM144B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714002 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.23 | 17-MC-DCS-004 | TS-P-03 | 23 | 24 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144B | 17-P-144B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:24/ O1011206:25A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -144 -B | 17XYSTM144B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714002 | DCS_DO_03 | MCC |  | 17-I-CD-N-021BL02 | 30 Core | C.25 | 17-MC-DCS-004 | TS-P-03 | 25 | 26 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-144B | 17-P-144B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-03:26/ O1011206:26A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -A | 17TSHM145A |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714002 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.07 | 17-MC-DCS-002 | TS-O-08 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U7 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-145A | 17-P-145A ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:13/ O1011100_U7:3 | TS-O-08:14/ O1011100_U7:4 |  |  | O1011100:7A/ O1011100_U7:5 | O1011100:7B/ O1011100_U7:6 | [6 empty] | 7A | 7B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -A | 17XSLM145A |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714002 | DCS_DI_04 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.15 | 17-MC-DCS-002 | TS-O-08 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U23 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-145A | 17-P-145A УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:29/ O1011100_U23:3 | TS-O-08:30/ O1011100_U23:1 |  |  | O1011100:23A/ O1011100_U23:7 | O1011100:23B/ O1011100_U23:8 | [6 empty] | 23A | 23B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -A | 17XSM145A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.13 | 17-MC-DCS-004 | TS-R-02 | 25 | 26 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145A | P145A НАСОС АВАРИЙНОГО ПЕРЕЛИВА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:25/ O1011108:11A | TS-R-02:26/ O1011108:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -A | 17XSAM145A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.14 | 17-MC-DCS-004 | TS-R-02 | 27 | 28 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145A | 17-P-145A ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:27/ O1011108:12A | TS-R-02:28/ O1011108:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -A | 17XSRM145A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.15 | 17-MC-DCS-004 | TS-R-02 | 29 | 30 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145A | 17-P-145A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:29/ O1011108:13A | TS-R-02:30/ O1011108:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -A | 17XYSPM145A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714002 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.01 | 17-MC-DCS-004 | TS-P-04 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145A | 17-P-145A СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:2/ O1011206:27A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -A | 17XYSTM145A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714002 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.03 | 17-MC-DCS-004 | TS-P-04 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145A | 17-P-145A ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:4/ O1011206:28A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -B | 17TSHM145B |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Overtemperature Command | 4124-XZ-DM-21714002 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.08 | 17-MC-DCS-002 | TS-O-08 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U8 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-145B | 17-P-145B ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:15/ O1011100_U8:3 | TS-O-08:16/ O1011100_U8:4 |  |  | O1011100:8A/ O1011100_U8:5 | O1011100:8B/ O1011100_U8:6 | [6 empty] | 8A | 8B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -B | 17XSLM145B |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Command | 4124-XZ-DM-21714002 | DCS_DI_04 | Field |  | 17-C-DD-N-001FL14 | 24 Pair | Pr.16 | 17-MC-DCS-002 | TS-O-08 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U24 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Pump 17-P-145B | 17-P-145B УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-08:31/ O1011100_U24:3 | TS-O-08:32/ O1011100_U24:1 |  |  | O1011100:24A/ O1011100_U24:7 | O1011100:24B/ O1011100_U24:8 | [6 empty] | 24A | 24B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -B | 17XSM145B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.16 | 17-MC-DCS-004 | TS-R-02 | 31 | 32 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145B | P145B НАСОС АВАРИЙНОГО ПЕРЕЛИВА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:31/ O1011108:14A | TS-R-02:32/ O1011108:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -B | 17XSAM145B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.17 | 17-MC-DCS-004 | TS-R-02 | 33 | 34 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145B | 17-P-145B ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:33/ O1011108:15A | TS-R-02:34/ O1011108:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -B | 17XSRM145B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714002 | DCS_DI_03 | MCC |  | 17-I-DD-N-011BL02 | 24 Pair | Pr.18 | 17-MC-DCS-004 | TS-R-02 | 35 | 36 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145B | 17-P-145B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-02:35/ O1011108:16A | TS-R-02:36/ O1011108:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -B | 17XYSPM145B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714002 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.05 | 17-MC-DCS-004 | TS-P-04 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145B | 17-P-145B СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:6/ O1011206:29A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -145 -B | 17XYSTM145B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714002 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.07 | 17-MC-DCS-004 | TS-P-04 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water retaintion Pump 17-P-145B | 17-P-145B ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:8/ O1011206:30A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -A | 17TSHM146LPA |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714003 | DCS_DI_02 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.04 | 17-MC-DCS-002 | TS-Q-13 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U12 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPA | 17-P-146LPA ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:7/ O1011100_U12:3 | TS-Q-13:8/ O1011100_U12:4 |  |  | O1011100:12A/ O1011100_U12:5 | O1011100:12B/ O1011100_U12:6 | [6 empty] | 12A | 12B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -A | 17XSLM146LPA |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714003 | DCS_DI_04 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.03 | 17-MC-DCS-002 | TS-Q-13 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U28 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPA | 17-P-146LPA УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:5/ O1011100_U28:3 | TS-Q-13:6/ O1011100_U28:1 |  |  | O1011100:28A/ O1011100_U28:7 | O1011100:28B/ O1011100_U28:8 | [6 empty] | 28A | 28B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -A | 17XSM146LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.01 | 17-MC-DCS-004 | TS-Q-01 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPA | P146LPA НАСОС КНС ЗАГРЯЗНЕННЫЙ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:1/ O1011109:15A | TS-Q-01:2/ O1011109:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -A | 17XSAM146LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.02 | 17-MC-DCS-004 | TS-Q-01 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPA | 17-P-146LPA ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:3/ O1011109:16A | TS-Q-01:4/ O1011109:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -A | 17XSRM146LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.03 | 17-MC-DCS-004 | TS-Q-01 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPA | 17-P-146LPA МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:5/ O1011109:17A | TS-Q-01:6/ O1011109:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -A | 17XYSPM146LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.25 | 17-MC-DCS-004 | TS-P-04 | 25 | 26 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPA | 17-P-146LPA СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:26/ O1011207:7A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -A | 17XYSTM146LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-022BL02 | 30 Core | C.27 | 17-MC-DCS-004 | TS-P-04 | 27 | 28 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPA | P140LPB НАСОС КНС 1 ЛИВНЕВЫЙ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-04:28/ O1011207:8A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -B | 17TSHM146LPB |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714003 | DCS_DI_02 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.10 | 17-MC-DCS-002 | TS-Q-13 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U15 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPB | 17-P-146LPB ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:19/ O1011100_U15:3 | TS-Q-13:20/ O1011100_U15:4 |  |  | O1011100:15A/ O1011100_U15:5 | O1011100:15B/ O1011100_U15:6 | [6 empty] | 15A | 15B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -B | 17XSLM146LPB |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714003 | DCS_DI_04 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.09 | 17-MC-DCS-002 | TS-Q-13 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U31 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPB | 17-P-146LPB УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:17/ O1011100_U31:3 | TS-Q-13:18/ O1011100_U31:1 |  |  | O1011100:31A/ O1011100_U31:7 | O1011100:31B/ O1011100_U31:8 | [6 empty] | 31A | 31B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -B | 17XSM146LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.04 | 17-MC-DCS-004 | TS-Q-01 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPB | P146LPB НАСОС КНС ЗАГРЯЗНЕННЫЙ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:7/ O1011109:18A | TS-Q-01:8/ O1011109:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -B | 17XSAM146LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.05 | 17-MC-DCS-004 | TS-Q-01 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPB | 17-P-146LPB ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:9/ O1011109:19A | TS-Q-01:10/ O1011109:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -B | 17XSRM146LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.06 | 17-MC-DCS-004 | TS-Q-01 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPB | 17-P-146LPB МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:11/ O1011109:20A | TS-Q-01:12/ O1011109:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -B | 17XYSPM146LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-023BL02 | 30 Core | C.01 | 17-MC-DCS-004 | TS-P-05 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPB | 17-P-146LPB СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-05:2/ O1011207:9A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -146LP -B | 17XYSTM146LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-023BL02 | 30 Core | C.03 | 17-MC-DCS-004 | TS-P-05 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-146LPB | P140LPB НАСОС КНС 1 ЛИВНЕВЫЙ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-05:4/ O1011207:10A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -A | 17TSHM147LPA |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714003 | DCS_DI_02 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.06 | 17-MC-DCS-002 | TS-Q-13 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U13 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPA | 17-P-147LPA ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:11/ O1011100_U13:3 | TS-Q-13:12/ O1011100_U13:4 |  |  | O1011100:13A/ O1011100_U13:5 | O1011100:13B/ O1011100_U13:6 | [6 empty] | 13A | 13B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -A | 17XSLM147LPA |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714003 | DCS_DI_04 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.05 | 17-MC-DCS-002 | TS-Q-13 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U29 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPA | 17-P-147LPA УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:9/ O1011100_U29:3 | TS-Q-13:10/ O1011100_U29:1 |  |  | O1011100:29A/ O1011100_U29:7 | O1011100:29B/ O1011100_U29:8 | [6 empty] | 29A | 29B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -A | 17XSM147LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.07 | 17-MC-DCS-004 | TS-Q-01 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPA | P147LPA НАСОС КНС МАСЛО-ЗАГРЯЗН. | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:13/ O1011109:21A | TS-Q-01:14/ O1011109:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -A | 17XSAM147LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.08 | 17-MC-DCS-004 | TS-Q-01 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPA | 17-P-147LPA ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:15/ O1011109:22A | TS-Q-01:16/ O1011109:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -A | 17XSRM147LPA |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.09 | 17-MC-DCS-004 | TS-Q-01 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPA | 17-P-147LPA МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:17/ O1011109:23A | TS-Q-01:18/ O1011109:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -A | 17XYSPM147LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-023BL02 | 30 Core | C.05 | 17-MC-DCS-004 | TS-P-05 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPA | 17-P-147LPA СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-05:6/ O1011207:11A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -A | 17XYSTM147LPA |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-023BL02 | 30 Core | C.07 | 17-MC-DCS-004 | TS-P-05 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPA | 17-P-147LPA ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-05:8/ O1011207:12A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -B | 17TSHM147LPB |  | DI-NIS (Thermistors PTC) DCS |  | Сигнал | Motor Over temperature Status | 4124-XZ-DM-21714003 | DCS_DI_02 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.12 | 17-MC-DCS-002 | TS-Q-13 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U16 | HD5516 | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPB | 17-P-147LPB ВЫСОКАЯ ТЕМПЕРАТУРА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:23/ O1011100_U16:3 | TS-Q-13:24/ O1011100_U16:4 |  |  | O1011100:16A/ O1011100_U16:5 | O1011100:16B/ O1011100_U16:6 | [6 empty] | 16A | 16B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -B | 17XSLM147LPB |  | DI-NIS (Conductivity) DCS |  | Сигнал | Motor Leakage Status | 4124-XZ-DM-21714003 | DCS_DI_04 | Field |  | 17-J-DD-N-002FL14 | 24 Pair | Pr.11 | 17-MC-DCS-002 | TS-Q-13 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011100_U32 | KFD2-ER-1.W.LB | O1011100 | TUA711-DIO32 | 17-SC-DCS-002/O1011100/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011100 | 1 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPB | 17-P-147LPB УТЕЧКА | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-13:21/ O1011100_U32:3 | TS-Q-13:22/ O1011100_U32:1 |  |  | O1011100:32A/ O1011100_U32:7 | O1011100:32B/ O1011100_U32:8 | [6 empty] | 32A | 32B | 3 | 1 |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -B | 17XSM147LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.10 | 17-MC-DCS-004 | TS-Q-01 | 19 | 20 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPB | P147LPA НАСОС КНС МАСЛО-ЗАГРЯЗН. | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:19/ O1011109:24A | TS-Q-01:20/ O1011109:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -B | 17XSAM147LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.11 | 17-MC-DCS-004 | TS-Q-01 | 21 | 22 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPB | 17-P-147LPB ДОСТУПНО | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:21/ O1011109:25A | TS-Q-01:22/ O1011109:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -B | 17XSRM147LPB |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21714003 | DCS_DI_03 | MCC |  | 17-I-DD-N-024BL02 | 24 Pair | Pr.12 | 17-MC-DCS-004 | TS-Q-01 | 23 | 24 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011109 | TUA711-DIO32 | 17-SC-DCS-002/O1011109/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011109 | 10 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPB | 17-P-147LPB МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-Q-01:23/ O1011109:26A | TS-Q-01:24/ O1011109:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -B | 17XYSPM147LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-023BL02 | 30 Core | C.09 | 17-MC-DCS-004 | TS-P-05 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPB | 17-P-147LPB СТОП | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-05:10/ O1011207:13A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -147LP -B | 17XYSTM147LPB |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21714003 | DCS_DO_03 | MCC |  | 17-I-CD-N-023BL02 | 30 Core | C.11 | 17-MC-DCS-004 | TS-P-05 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011207 | TUA711-DIO32 | 17-SC-DCS-002/O1011207/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011207 | 8 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Rain Water Contaminated Water lift 17-P-147LPB | 17-P-147LPB ПУСК | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-P-05:12/ O1011207:14A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -A | 17XSM171A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21717101 | DCS_DI_03 | MCC |  | 17-I-DD-N-012BL02 | 24 Pair | Pr.01 | 17-MC-DCS-004 | TS-R-03 | 1 | 2 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171A Centrifugal Pumps | P171A НАСОС ГЛИКОЛЕВОЙ ВОДЫ | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:1/ O1011108:17A | TS-R-03:2/ O1011108:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -A | 17XSAM171A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21717101 | DCS_DI_03 | MCC |  | 17-I-DD-N-012BL02 | 24 Pair | Pr.02 | 17-MC-DCS-004 | TS-R-03 | 3 | 4 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171A Centrifugal Pumps | 17-P-171A ДОСТУПНО | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:3/ O1011108:18A | TS-R-03:4/ O1011108:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -A | 17XSRM171A |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21717101 | DCS_DI_03 | MCC |  | 17-I-DD-N-012BL02 | 24 Pair | Pr.03 | 17-MC-DCS-004 | TS-R-03 | 5 | 6 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171A Centrifugal Pumps | 17-P-171A МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:5/ O1011108:19A | TS-R-03:6/ O1011108:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -A | 17XYSPM171A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21717101 | DCS_DO_03 | MCC |  | 17-I-CD-N-015BL02 | 30 Core | C.01 | 17-MC-DCS-004 | TS-O-04 | 1 | 2 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171A Centrifugal Pumps | 17-P-171A СТОП | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-04:2/ O1011206:8A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -A | 17XYSTM171A |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21717101 | DCS_DO_03 | MCC |  | 17-I-CD-N-015BL02 | 30 Core | C.03 | 17-MC-DCS-004 | TS-O-04 | 3 | 4 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171A Centrifugal Pumps | 17-P-171A ПУСК | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-04:4/ O1011206:9A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -B | 17XSM171B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21717101 | DCS_DI_03 | MCC |  | 17-I-DD-N-012BL02 | 24 Pair | Pr.04 | 17-MC-DCS-004 | TS-R-03 | 7 | 8 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171B Centrifugal Pumps | P171B НАСОС ГЛИКОЛЕВОЙ ВОДЫ | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:7/ O1011108:20A | TS-R-03:8/ O1011108:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -B | 17XSAM171B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21717101 | DCS_DI_03 | MCC |  | 17-I-DD-N-012BL02 | 24 Pair | Pr.05 | 17-MC-DCS-004 | TS-R-03 | 9 | 10 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171B Centrifugal Pumps | 17-P-171B ДОСТУПНО | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:9/ O1011108:21A | TS-R-03:10/ O1011108:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -B | 17XSRM171B |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21717101 | DCS_DI_03 | MCC |  | 17-I-DD-N-012BL02 | 24 Pair | Pr.06 | 17-MC-DCS-004 | TS-R-03 | 11 | 12 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171B Centrifugal Pumps | 17-P-171B МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:11/ O1011108:22A | TS-R-03:12/ O1011108:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -B | 17XYSPM171B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21717101 | DCS_DO_03 | MCC |  | 17-I-CD-N-015BL02 | 30 Core | C.05 | 17-MC-DCS-004 | TS-O-04 | 5 | 6 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171B Centrifugal Pumps | 17-P-171B СТОП | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-04:6/ O1011206:10A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -171 -B | 17XYSTM171B |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21717101 | DCS_DO_03 | MCC |  | 17-I-CD-N-015BL02 | 30 Core | C.07 | 17-MC-DCS-004 | TS-O-04 | 7 | 8 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-171B Centrifugal Pumps | 17-P-171B ПУСК | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-04:8/ O1011206:11A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -172 | 17XSM172 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Running status | 4124-XZ-DM-21717101 | DCS_DI_03 | MCC |  | 17-I-DD-N-012BL02 | 24 Pair | Pr.07 | 17-MC-DCS-004 | TS-R-03 | 13 | 14 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Glycol water filling | P172 НАСОС ПОДПИТКИ ГЛИК. ВОДЫ | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | RUNNING | NOT RUNNING | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:13/ O1011108:23A | TS-R-03:14/ O1011108:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -172 | 17XSAM172 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Available status | 4124-XZ-DM-21717101 | DCS_DI_03 | MCC |  | 17-I-DD-N-012BL02 | 24 Pair | Pr.08 | 17-MC-DCS-004 | TS-R-03 | 15 | 16 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Glycol water filling | 17-P-172 ДОСТУПНО | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:15/ O1011108:24A | TS-R-03:16/ O1011108:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -172 | 17XSRM172 |  | DI-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Remote status | 4124-XZ-DM-21717101 | DCS_DI_03 | MCC |  | 17-I-DD-N-012BL02 | 24 Pair | Pr.09 | 17-MC-DCS-004 | TS-R-03 | 17 | 18 |  | 48 | ASK 3MLD, ASK 3MB |  |  | O1011108 | TUA711-DIO32 | 17-SC-DCS-002/O1011108/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011108 | 9 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Glycol water filling | 17-P-172 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-R-03:17/ O1011108:25A | TS-R-03:18/ O1011108:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -172 | 17XYSPM172 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Stop command | 4124-XZ-DM-21717101 | DCS_DO_03 | MCC |  | 17-I-CD-N-015BL02 | 30 Core | C.09 | 17-MC-DCS-004 | TS-O-04 | 9 | 10 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Glycol water filling | 17-P-172 СТОП | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | NO ACTION | STOP | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-04:10/ O1011206:12A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-M -172 | 17XYSTM172 |  | DO-NIS (MCC 230VAC) DCS |  | Сигнал | Motor Start command | 4124-XZ-DM-21717101 | DCS_DO_03 | MCC |  | 17-I-CD-N-015BL02 | 30 Core | C.11 | 17-MC-DCS-004 | TS-O-04 | 11 | 12 |  | 30 | ASK 3MLD, ASK 3MB |  |  | O1011206 | TUA711-DIO32 | 17-SC-DCS-002/O1011206/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011206 | 7 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Glycol water filling | 17-P-172 ПУСК | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | START | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [20 empty] | TS-O-04:12/ O1011206:13A | [11 empty] | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-M-070001 | 17MXSA070001 |  | DI-NIS (VFC) DCS | 24.09.24 сигнал, кабель, клемник добавлен по TQ_ALL_81 | Сигнал | MOV Available | 4124-FY-VD-BD17217L07300001 | DCS_DI_01 |  |  | 17-C-DD-N-001FL07-L073 | 06 Pair | Pr. 1 | 17-MC-DCS-002 | TS-P-10 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 20 | DI715-S11 | 32 |  |  | добавить клеммник, смонтировать провода от клемника до терм платы | DCS AMMONIA-UTILITIES | 17-MOV-070001 AVAILABLE | 17-MOV-070001 Доступна | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-P-10:1/ O1010204:20A | TS-P-10:2/ O1010204:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-M-070001 | 17MXSR070001 |  | DI-NIS (VFC) DCS | 24.09.24 сигнал, кабель, клемник добавлен по TQ_ALL_81 | Сигнал | MOV Remote | 4124-FY-VD-BD17217L07300001 | DCS_DI_01 |  |  | 17-C-DD-N-001FL07-L073 | 06 Pair | Pr. 2 | 17-MC-DCS-002 | TS-P-10 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 21 | DI715-S11 | 32 |  |  | добавить клеммник, смонтировать провода от клемника до терм платы | DCS AMMONIA-UTILITIES | 17-MOV-070001 REMOTE | 17-MOV-070001 Мест/дист. | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-P-10:3/ O1010204:21A | TS-P-10:4/ O1010204:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-M-070001 | 17MZSL070001 |  | DI-NIS (VFC) DCS | 24.09.24 сигнал, кабель, клемник добавлен по TQ_ALL_81 | Сигнал | MOV Closed | 4124-FY-VD-BD17217L07300001 | DCS_DI_01 |  |  | 17-C-DD-N-001FL07-L073 | 06 Pair | Pr. 3 | 17-MC-DCS-002 | TS-P-10 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 22 | DI715-S11 | 32 |  |  | добавить клеммник, смонтировать провода от клемника до терм платы | DCS AMMONIA-UTILITIES | 17-MOV-070001 CLOSED | 17-MOV-070001 Закрыта | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-P-10:5/ O1010204:22A | TS-P-10:6/ O1010204:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-M-070001 | 17MZSH070001 |  | DI-NIS (VFC) DCS | 24.09.24 сигнал, кабель, клемник добавлен по TQ_ALL_81 | Сигнал | MOV Open | 4124-FY-VD-BD17217L07300001 | DCS_DI_01 |  |  | 17-C-DD-N-001FL07-L073 | 06 Pair | Pr. 4 | 17-MC-DCS-002 | TS-P-10 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 23 | DI715-S11 | 32 |  |  | добавить клеммник, смонтировать провода от клемника до терм платы | DCS AMMONIA-UTILITIES | 17-MOV-070001 OPENED | 17-MOV-070001 Открыта | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-P-10:7/ O1010204:23A | TS-P-10:8/ O1010204:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-M-070001 | 17MXYH070001 |  | DO-NIS (24VDC) DCS | 24.09.24 сигнал 17XYST1M072LPA, кабель удалены по TQ_ALL_81 сигнал, кабель добавлены по TQ_ALL_81 | Сигнал | MOV Open command | 4124-FY-VD-BD17217L07300001 | DCS_DO_01 |  |  | 17-C-CD-N-002FL07-L073 | 16 Core | C.01 | 17-MC-DCS-002 | TS-O-02 | 1 | 2 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 9 | DO716-S11 | 32 | 0.1 |  | изменить количество клемм с 30 до 16, изменить маркировку клеммной группы | DCS AMMONIA-UTILITIES | 17-MOV-070001 Close CMD | 17-MOV-070001 Закрыть | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-O-02:1/ O1011202:9A | TS-O-02:2/ O1011202:9C | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.5 | 17-M-070001 | 17MXYL070001 |  | DO-NIS (24VDC) DCS | 24.09.24 сигнал 17XYST2M072LPA, кабель удалены по TQ_ALL_81 сигнал, кабель добавлены по TQ_ALL_81 | Сигнал | MOV Close command | 4124-FY-VD-BD17217L07300001 | DCS_DO_01 |  |  | 17-C-CD-N-002FL07-L073 | 16 Core | C.03 | 17-MC-DCS-002 | TS-O-02 | 3 | 4 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 10 | DO716-S11 | 32 | 0.1 |  | изменить количество клемм с 30 до 16, изменить маркировку клеммной группы | DCS AMMONIA-UTILITIES | 17-MOV-070001 Open CMD | 17-MOV-070001 Открыть | 17-AMMONIA UTILITIES |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-O-02:3/ O1011202:10A | TS-O-02:4/ O1011202:10C | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-MOV-0001 | 17MZSH0001 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Open |  | DCS_DI_01 | Field |  | 17-C-DD-N-1-FL50 | 10 Pair | Pr.01 | 17-MC-DCS-001 | TS-H-03 | 1 | 2 |  | 20 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CO2 from Ammonia 2 to Urea | 17-MOV-0001 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-03:1/ O1010200:27A | TS-H-03:2/ O1010200:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-MOV-0001 | 17MZSL0001 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Closed |  | DCS_DI_01 | Field |  | 17-C-DD-N-1-FL50 | 10 Pair | Pr.02 | 17-MC-DCS-001 | TS-H-03 | 3 | 4 |  | 20 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CO2 from Ammonia 2 to Urea | 17-MOV-0001 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-03:3/ O1010200:28A | TS-H-03:4/ O1010200:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-MOV-0001 | 17MXSA0001 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Available |  | DCS_DI_01 | Field |  | 17-C-DD-N-1-FL50 | 10 Pair | Pr.03 | 17-MC-DCS-001 | TS-H-03 | 5 | 6 |  | 20 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CO2 from Ammonia 2 to Urea | 17-MOV-0001 ДОСТУПНО | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | AVAILABLE | NOT AVLB | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-03:5/ O1010200:29A | TS-H-03:6/ O1010200:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-MOV-0001 | 17MXSR0001 |  | DI-NIS (VFC) DCS |  | Сигнал | MOV Remote |  | DCS_DI_01 | Field |  | 17-C-DD-N-1-FL50 | 10 Pair | Pr.04 | 17-MC-DCS-001 | TS-H-03 | 7 | 8 |  | 20 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CO2 from Ammonia 2 to Urea | 17-MOV-0001 МЕСТ/ДИСТАНЦ | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | REMOTE | LOCAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-03:7/ O1010200:30A | TS-H-03:8/ O1010200:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-MOV-0001 | 17MXYH0001 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Open command |  | DCS_DO_01 | Field |  | 17-C-СD-N-1-FL50 | 20 Core | C.01 | 17-MC-DCS-001 | TS-H-04 | 1 | 2 |  | 20 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 28 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | CO2 from Ammonia 2 to Urea | 17-MOV-0001 ОТКРЫТЬ | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-04:1/ O1010211:28A | TS-H-04:2/ O1010211:28C | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-MOV-0001 | 17MXYL0001 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Close command |  | DCS_DO_01 | Field |  | 17-C-СD-N-1-FL50 | 20 Core | C.03 | 17-MC-DCS-001 | TS-H-04 | 3 | 4 |  | 20 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 29 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | CO2 from Ammonia 2 to Urea | 17-MOV-0001 ЗАКРЫТЬ | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-04:3/ O1010211:29A | TS-H-04:4/ O1010211:29C | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-MOV-0001 | 17MXYSP0001 |  | DO-NIS (24VDC) DCS |  | Сигнал | MOV Stop command |  | DCS_DO_01 | Field |  | 17-C-СD-N-1-FL50 | 20 Core | C.05 | 17-MC-DCS-001 | TS-H-04 | 5 | 6 |  | 20 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 30 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | CO2 from Ammonia 2 to Urea | 17-MOV-0001 ОСТАНОВИТЬ | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | STOP | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | % | [12 empty] | TS-H-04:5/ O1010211:30A | TS-H-04:6/ O1010211:30C | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -090110 | 17YS090110Y |  | DO-NIS (VFC NO) DCS |  | Сигнал | Exchange Signal | 4124-GY-VD-BD17517L091090 | DCS_DO_02 | RR-AM |  | 17-I-DD-N-001BL02-L091 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-H-06 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Intertrip signal for process trip ( IA) Compressor A | ПУСК КОМПРЕССОРА А | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC | TRIP | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-06:1/ O1011211:9A | TS-H-06:2/ O1011211:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -090111 | 17YS090111Y |  | DO-NIS (VFC NO) DCS |  | Сигнал | Exchange Signal | 4124-GY-VD-BD17517L091090 | DCS_DO_02 | RR-AM |  | 17-I-DD-N-001BL02-L091 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-H-06 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Intertrip signal for process trip ( IA) Compressor B | СТОП КОМПРЕССОРА А | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC | [22 empty] | TS-H-06:3/ O1011211:10A | TS-H-06:4/ O1011211:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -090210 | 17YS090210Y |  | DO-NIS (VFC NO) DCS |  | Сигнал | Exchange Signal | 4124-GY-VD-BD17517L091090 | DCS_DO_02 | RR-AM |  | 17-I-DD-N-002BL02-L091 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-H-05 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Intertrip signal for process trip ( IA) Compressor B | ПУСК КОМПРЕССОРА В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC | TRIP | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:1/ O1011211:7A | TS-H-05:2/ O1011211:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -090211 | 17YS090211Y |  | DO-NIS (VFC NO) DCS |  | Сигнал | Exchange Signal | 4124-GY-VD-BD17517L091090 | DCS_DO_02 | RR-AM |  | 17-I-DD-N-002BL02-L091 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-H-05 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Intertrip signal for process trip ( IA) Compressor A | СТОП КОМПРЕССОРА В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC | TRIP | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:3/ O1011211:8A | TS-H-05:4/ O1011211:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -00008 | 17PT00008 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21709002 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL10 | 12 Pair | Pr.03 | 17-MC-DCS-009 | TS-G-01 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U3 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From Inst Air Unit 7-L-091 | ВОЗДУХ КИП В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1.5 | MPa | [5 empty] | TS-G-01:5/ O1010011_U3:3 | TS-G-01:6/ O1010011_U3:4 |  |  | O1010011:3A/ O1010011_U3:5 | O1010011:3C/ O1010011_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -00010 | 17PT00010 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21709001 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL10 | 12 Pair | Pr.04 | 17-MC-DCS-009 | TS-G-01 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U4 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Inst Air Unit 7-L-091 | ТЕХНИЧЕСКИЙ ВОЗДУХ В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1.5 | MPa | [5 empty] | TS-G-01:7/ O1010011_U4:3 | TS-G-01:8/ O1010011_U4:4 |  |  | O1010011:4A/ O1010011_U4:5 | O1010011:4C/ O1010011_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -00014 | 17PT00014 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | O2 Analyzer Transmitter | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.08 | 17-MC-DCS-009 | TS-H-03 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U3 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP steam to Dearetor | LS НА ВХОДЕ В ДЕАЭРАТОР | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 0.7 | MPa | [5 empty] | TS-H-03:15/ O1011006_U3:3 | TS-H-03:16/ O1011006_U3:4 |  |  | O1011006:3A/ O1011006_U3:5 | O1011006:3C/ O1011006_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -020207 -A | 17PDT020207A |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.06 | 17-MC-DCS-008 | TS-O-03 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011002_U8 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Cationic trap | ВЫХОД C ФСД S-021A | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.1 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-03:11/ O1011002_U8:3 | TS-O-03:12/ O1011002_U8:4 |  |  | O1011002:8A/ O1011002_U8:5 | O1011002:8C/ O1011002_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -020207 -B | 17PDT020207B |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.11 | 17-MC-DCS-008 | TS-O-03 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U9 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Cationic trap | ВЫХОД C ФСД S-021В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.1 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-03:21/ O1011003_U9:3 | TS-O-03:22/ O1011003_U9:4 |  |  | O1011003:9A/ O1011003_U9:5 | O1011003:9C/ O1011003_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -020207 -C | 17PDT020207C |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.16 | 17-MC-DCS-008 | TS-O-03 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U12 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Cationic trap | ВЫХОД C ФСД S-021С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.1 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-03:31/ O1011003_U12:3 | TS-O-03:32/ O1011003_U12:4 |  |  | O1011003:12A/ O1011003_U12:5 | O1011003:12C/ O1011003_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -02083 | 17PT02083 |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21702020 | DCS_AI_02 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.07 | 17-MC-DCS-006 | TS-Q-05 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U9 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-021 Pressure | ДАВЛЕНИЕ В БАКЕ 17-T-021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -1 | 6 | kPa | [5 empty] | TS-Q-05:13/ O1010014R_U9:3 | TS-Q-05:14/ O1010014R_U9:4 |  |  | O1010014R:9A/ O1010014R_U9:5 | O1010014R:9C/ O1010014R_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -02083 | 17PY02083A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21702020 | DCS_AO_02 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.09 | 17-MC-DCS-006 | TS-Q-05 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U16 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 16 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-021 Pressure | ДАВЛЕНИЕ В БАКЕ 17-T-021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-05:17/ O1010104R_U16:3 | TS-Q-05:18/ O1010104R_U16:4 |  |  | O1010104R:16A/ O1010104R_U16:5 | O1010104R:16C/ O1010104R_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -02083 | 17PY02083B |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21702020 | DCS_AO_02 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.10 | 17-MC-DCS-006 | TS-Q-05 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010106R_U8 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 8 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-021 Pressure | ДАВЛЕНИЕ В БАКЕ 17-T-021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-05:19/ O1010106R_U8:3 | TS-Q-05:20/ O1010106R_U8:4 |  |  | O1010106R:8A/ O1010106R_U8:5 | O1010106R:8C/ O1010106R_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -02088 | 17PT02088 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21702020 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.13 | 17-MC-DCS-006 | TS-Q-04 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U5 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 17-P-021 discharge to stripper | ДАВЛЕНИЕ НА НАГНЕТАНИИ 17-P-021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 4.9 | 5.9 |  | 0 | 9 | MPa | [5 empty] | TS-Q-04:25/ O1010005_U5:3 | TS-Q-04:26/ O1010005_U5:4 |  |  | O1010005:5A/ O1010005_U5:5 | O1010005:5C/ O1010005_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -03006 | 17PT03006 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21703001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.08 | 17-MC-DCS-006 | TS-O-02 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U8 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 17-P-032A/B/C discharge line | ДАВЛЕНИЕ НА НАГНЕТ 17-P-032A/B/C | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.88 | 1 |  | 0 | 2 | MPa | [5 empty] | TS-O-02:15/ O1010002_U8:3 | TS-O-02:16/ O1010002_U8:4 |  |  | O1010002:8A/ O1010002_U8:5 | O1010002:8C/ O1010002_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -03007 | 17PT03007 |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21703001 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.09 | 17-MC-DCS-006 | TS-O-02 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U12 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-032 Pressure | ДАВЛЕНИЕ В БАКЕ ДЕМ ВОДЫ 17T-032 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -1 | 6 | kPa | [5 empty] | TS-O-02:17/ O1010012R_U12:3 | TS-O-02:18/ O1010012R_U12:4 |  |  | O1010012R:12A/ O1010012R_U12:5 | O1010012R:12C/ O1010012R_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -03007 | 17PY03007A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21703001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.13 | 17-MC-DCS-006 | TS-O-02 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U13 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 13 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Nitrogen from Header | АЗОТ ИЗ КОЛЛЕКТОРА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-02:25/ O1010104R_U13:3 | TS-O-02:26/ O1010104R_U13:4 |  |  | O1010104R:13A/ O1010104R_U13:5 | O1010104R:13C/ O1010104R_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -03007 | 17PY03007B |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21703001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.14 | 17-MC-DCS-006 | TS-O-02 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010106R_U1 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 1 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Nitrogen from Header | АЗОТ ИЗ КОЛЛЕКТОРА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-02:27/ O1010106R_U1:3 | TS-O-02:28/ O1010106R_U1:4 |  |  | O1010106R:1A/ O1010106R_U1:5 | O1010106R:1C/ O1010106R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -03021 | 17PT03021 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.14 | 17-MC-DCS-006 | TS-Q-04 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U6 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Process Condensate from 17-P-030 A/B/C | ТЕХНОЛ КОНД ОТ 17-P-030-A/B/C | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1.5 | MPa | [5 empty] | TS-Q-04:27/ O1010005_U6:3 | TS-Q-04:28/ O1010005_U6:4 |  |  | O1010005:6A/ O1010005_U6:5 | O1010005:6C/ O1010005_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -03066 | 17PT03066 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21703003 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.08 | 17-MC-DCS-006 | TS-Q-05 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U15 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-031A/B/C discharge to 17-S-022A/B/C | ДАВЛЕНИЕ НАГНЕТ 17-P-031A/B/C | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1.5 | MPa | [5 empty] | TS-Q-05:15/ O1010005_U15:3 | TS-Q-05:16/ O1010005_U15:4 |  |  | O1010005:15A/ O1010005_U15:5 | O1010005:15C/ O1010005_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -07033 | 17PT07033 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707003 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL07 | 12 Pair | Pr.03 | 17-MC-DCS-006 | TS-O-01 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010000_U5 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | AUTOSTART 17-P-071A-G | НАГНЕТАНИЕ НАСОСОВ 17-P-071A-G | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  |  | 0 | 1 | MPa | [5 empty] | TS-O-01:5/ O1010000_U5:3 | TS-O-01:6/ O1010000_U5:4 |  |  | O1010000:5A/ O1010000_U5:5 | O1010000:5C/ O1010000_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -07041 | 17PT07041 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707003 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.08 | 17-MC-DCS-006 | TS-Q-03 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U3 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump Basin to CWS distribution header | НАГНЕТАНИЕ НАСОСА 17-P-071A | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  | 0.65 | 0 | 1 | MPa | [5 empty] | TS-Q-03:15/ O1010006_U3:3 | TS-Q-03:16/ O1010006_U3:4 |  |  | O1010006:3A/ O1010006_U3:5 | O1010006:3C/ O1010006_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -07042 | 17PT07042 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707003 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL07 | 12 Pair | Pr.04 | 17-MC-DCS-006 | TS-O-01 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010000_U6 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump Basin to CWS distribution header | НАГНЕТАНИЕ НАСОСА 17-P-071B | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  | 0.65 | 0 | 1 | MPa | [5 empty] | TS-O-01:7/ O1010000_U6:3 | TS-O-01:8/ O1010000_U6:4 |  |  | O1010000:6A/ O1010000_U6:5 | O1010000:6C/ O1010000_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -07043 | 17PT07043 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707003 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL07 | 12 Pair | Pr.05 | 17-MC-DCS-006 | TS-O-01 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010001_U1 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump Basin to CWS distribution header | НАГНЕТАНИЕ НАСОСА 17-P-071C | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  | 0.65 | 0 | 1 | MPa | [5 empty] | TS-O-01:9/ O1010001_U1:3 | TS-O-01:10/ O1010001_U1:4 |  |  | O1010001:1A/ O1010001_U1:5 | O1010001:1C/ O1010001_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -07044 | 17PT07044 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707003 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL07 | 12 Pair | Pr.06 | 17-MC-DCS-006 | TS-O-01 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010001_U2 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump Basin to CWS distribution header | НАГНЕТАНИЕ НАСОСА 17-P-071D | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  | 0.65 | 0 | 1 | MPa | [5 empty] | TS-O-01:11/ O1010001_U2:3 | TS-O-01:12/ O1010001_U2:4 |  |  | O1010001:2A/ O1010001_U2:5 | O1010001:2C/ O1010001_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -07045 | 17PT07045 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707007 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL07 | 12 Pair | Pr.07 | 17-MC-DCS-006 | TS-O-01 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010001_U3 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump Basin to CWS distribution header | НАГНЕТАНИЕ НАСОСА 17-P-071E | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  | 0.65 | 0 | 1 | MPa | [5 empty] | TS-O-01:13/ O1010001_U3:3 | TS-O-01:14/ O1010001_U3:4 |  |  | O1010001:3A/ O1010001_U3:5 | O1010001:3C/ O1010001_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -07046 | 17PT07046 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707007 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.09 | 17-MC-DCS-006 | TS-Q-03 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U4 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump Basin to CWS distribution header | НАГНЕТАНИЕ НАСОСА 17-P-071F | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  | 0.65 | 0 | 1 | MPa | [5 empty] | TS-Q-03:17/ O1010006_U4:3 | TS-Q-03:18/ O1010006_U4:4 |  |  | O1010006:4A/ O1010006_U4:5 | O1010006:4C/ O1010006_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -07047 | 17PT07047 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707007 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.10 | 17-MC-DCS-006 | TS-Q-03 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U5 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump Basin to CWS distribution header | НАГНЕТАНИЕ НАСОСА 17-P-071H | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  | 0.65 | 0 | 1 | MPa | [5 empty] | TS-Q-03:19/ O1010006_U5:3 | TS-Q-03:20/ O1010006_U5:4 |  |  | O1010006:5A/ O1010006_U5:5 | O1010006:5C/ O1010006_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -07048 | 17PT07048 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707007 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.11 | 17-MC-DCS-006 | TS-Q-03 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U6 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump Basin to Emergemncy CW | НАГНЕТАНИЕ НАСОСА 17-P-073A | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  | 0.68 | 0 | 1 | MPa | [5 empty] | TS-Q-03:21/ O1010006_U6:3 | TS-Q-03:22/ O1010006_U6:4 |  |  | O1010006:6A/ O1010006_U6:5 | O1010006:6C/ O1010006_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -07049 | 17PT07049 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707007 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.12 | 17-MC-DCS-006 | TS-Q-03 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U7 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CW Pump Basin to Emergemncy CW | НАГНЕТАНИЕ НАСОСА 17-P-073B | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  | 0.68 | 0 | 1 | MPa | [5 empty] | TS-Q-03:23/ O1010006_U7:3 | TS-Q-03:24/ O1010006_U7:4 |  |  | O1010006:7A/ O1010006_U7:5 | O1010006:7C/ O1010006_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -07050 | 17PT07050 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21707007 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.13 | 17-MC-DCS-006 | TS-Q-03 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U8 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Emergemncy CW to distribution header | НАГНЕТАНИЕ НАСОСОВ 17-P-073A/В | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  |  | 0 | 1 | MPa | [5 empty] | TS-Q-03:25/ O1010006_U8:3 | TS-Q-03:26/ O1010006_U8:4 |  |  | O1010006:8A/ O1010006_U8:5 | O1010006:8C/ O1010006_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -09001 | 17PT09001 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-XZ-DM-21709001 | DCS_AI_02 | Field |  | 17-C-AD-I-001FL10 | 12 Pair | Pr.05 | 17-MC-DCS-009 | TS-G-01 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010102R_U5 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Process air from Ammonia plant | ТЕХНОЛОГИЧЕСКИЙ ВОЗДУХ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.6 | 1.25 |  | 0 | 1.5 | MPa | [5 empty] | TS-G-01:9/ O1010102R_U5:3 | TS-G-01:10/ O1010102R_U5:4 |  |  | O1010102R:5A/ O1010102R_U5:5 | O1010102R:5C/ O1010102R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -09001 | 17PY09001 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21709001 | DCS_AO_02 | Field |  | 17-C-AD-I-001FL10 | 12 Pair | Pr.08 | 17-MC-DCS-009 | TS-G-01 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010110R_U5 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 5 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Process air from Ammonia plant | ТЕХНОЛОГ ВОЗДУХ С УСТАНОВКИ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-01:15/ O1010110R_U5:3 | TS-G-01:16/ O1010110R_U5:4 |  |  | O1010110R:5A/ O1010110R_U5:5 | O1010110R:5C/ O1010110R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -09022 | 17PT09022A |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21709002 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL10 | 12 Pair | Pr.06 | 17-MC-DCS-009 | TS-G-01 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U5 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-092B Vessel | РЕСИВЕР ВОЗДУХА КИП 17-V-092B | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.45 | 1.1 |  | 0 | 1.5 | MPa | [5 empty] | TS-G-01:11/ O1010011_U5:3 | TS-G-01:12/ O1010011_U5:4 |  |  | O1010011:5A/ O1010011_U5:5 | O1010011:5C/ O1010011_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -09022 | 17PT09022B |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21709002 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL10 | 12 Pair | Pr.07 | 17-MC-DCS-009 | TS-G-01 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U16 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-092A Vessel | РЕСИВЕР ВОЗДУХА КИП 17-V-092A | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.45 | 1.1 |  | 0 | 1.5 | MPa | [5 empty] | TS-G-01:13/ O1010011_U16:3 | TS-G-01:14/ O1010011_U16:4 |  |  | O1010011:16A/ O1010011_U16:5 | O1010011:16C/ O1010011_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -090330 | 17PT090330 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | H2O Analyzer Transmitter | 4124-GY-VD-BD17517L091091_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-I-004FL10-L091 | 12 Pair | Pr.06 | 17-MC-DCS-009 | TS-G-04 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011006_U12 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From 17-L-091-V-091 Separator | СЕПАРАТОР 17-L091-V-091 ВОЗД КИП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 0.6 | MPa | [5 empty] | TS-G-04:11/ O1011006_U12:3 | TS-G-04:12/ O1011006_U12:4 |  |  | O1011006:12A/ O1011006_U12:5 | O1011006:12C/ O1011006_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -10002 | 17PT10002 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21710001 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.04 | 17-MC-DCS-008 | TS-P-01 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010009_U2 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-106 Vessel | РЕСИВЕР АЗОТА 17-V-106 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.4 |  |  | 0 | 1.5 | MPa | [5 empty] | TS-P-01:7/ O1010009_U2:3 | TS-P-01:8/ O1010009_U2:4 |  |  | O1010009:2A/ O1010009_U2:5 | O1010009:2C/ O1010009_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -10008 | 17PT10008 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21710001 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.05 | 17-MC-DCS-008 | TS-P-01 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010009_U3 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | АЗОТ ИЗ 17-V-106 СЕТЬ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.4 |  |  | 0 | 1.5 | MPa | [5 empty] | TS-P-01:9/ O1010009_U3:3 | TS-P-01:10/ O1010009_U3:4 |  |  | O1010009:3A/ O1010009_U3:5 | O1010009:3C/ O1010009_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -10011 | 17PT10011 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21710001 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.06 | 17-MC-DCS-008 | TS-P-01 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010009_U4 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-103 Vessel | АЗОТ НД НА К-1 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.4 | 0.9 |  | 0 | 1.5 | MPa | [5 empty] | TS-P-01:11/ O1010009_U4:3 | TS-P-01:12/ O1010009_U4:4 |  |  | O1010009:4A/ O1010009_U4:5 | O1010009:4C/ O1010009_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -10015 | 17PT10015 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21710000 | DCS_AI_02 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.07 | 17-MC-DCS-008 | TS-P-01 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010100R_U2 | HD5542 | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP Steam to Header | ПАР НД ОТ АЗОТНОЙ УСТАНОВКИ В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.45 |  | 0 | 0.6 | MPa | [5 empty] | TS-P-01:13/ O1010100R_U2:3 | TS-P-01:14/ O1010100R_U2:4 |  |  | O1010100R:2A/ O1010100R_U2:5 | O1010100R:2C/ O1010100R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -10015 | 17PY10015 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21710000 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.08 | 17-MC-DCS-008 | TS-P-01 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010108R_U2 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 2 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP Steam to Header | ПАР НД В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-01:15/ O1010108R_U2:3 | TS-P-01:16/ O1010108R_U2:4 |  |  | O1010108R:2A/ O1010108R_U2:5 | O1010108R:2C/ O1010108R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -100703 | 17PT100703 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-GP-VD-BD17917K101004_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.01 | 17-MC-DCS-006 | TS-O-03 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U10 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 1st STAGE SUCTION PRESSURE | ВСАС 1 СТУПЕНИ 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.5 |  |  | 0 | 1.6 | Mpa | [5 empty] | TS-O-03:1/ O1010002_U10:3 | TS-O-03:2/ O1010002_U10:4 |  |  | O1010002:10A/ O1010002_U10:5 | O1010002:10C/ O1010002_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -100706 | 17PT100706 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-GP-VD-BD17917K101004_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.02 | 17-MC-DCS-006 | TS-O-03 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U11 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 1st STAGE DISHARGE PRESSURE | НАГНЕТАНИЕ 1 СТУПЕНИ 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 2.9 |  | 0 | 4 | Mpa | [5 empty] | TS-O-03:3/ O1010002_U11:3 | TS-O-03:4/ O1010002_U11:4 |  |  | O1010002:11A/ O1010002_U11:5 | O1010002:11C/ O1010002_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -100718 | 17PT100718 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-GP-VD-BD17917K101004_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.05 | 17-MC-DCS-006 | TS-O-03 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U13 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 2st STAGE DISHARGE PRESSURE | НАГНЕТАНИЕ 12СТУПЕНИ 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 6.7 |  | 0 | 10 | Mpa | [5 empty] | TS-O-03:9/ O1010002_U13:3 | TS-O-03:10/ O1010002_U13:4 |  |  | O1010002:13A/ O1010002_U13:5 | O1010002:13C/ O1010002_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -100727 | 17PT100727 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-GP-VD-BD17917K101004_SH.4 | DCS_AI_01 | LP |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.06 | 17-MC-DCS-006 | TS-O-03 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010000_U8 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CRANKCASE LUBE OIL PRESSURE | СМАЗ МАСЛО 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.35 |  |  | 0 | 1 | Mpa | [5 empty] | TS-O-03:11/ O1010000_U8:3 | TS-O-03:12/ O1010000_U8:4 |  |  | O1010000:8A/ O1010000_U8:5 | O1010000:8C/ O1010000_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -100747 | 17PT100747 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-GP-VD-BD17917K101004_SH.5 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.10 | 17-MC-DCS-006 | TS-O-03 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010003_U1 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | COOLING WATER INLET PRESSURE | ОВ НА 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.3 |  |  | 0 | 1 | Mpa | [5 empty] | TS-O-03:19/ O1010003_U1:3 | TS-O-03:20/ O1010003_U1:4 |  |  | O1010003:1A/ O1010003_U1:5 | O1010003:1C/ O1010003_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -100767 | 17PT100767 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-GP-VD-BD17917K101004_SH.4 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.13 | 17-MC-DCS-006 | TS-O-03 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010003_U4 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LUBE OIL CIRCUIT AUXILIARY OIL PUMP PRESSURE | НАГНЕТАНИЕ ПУСКОВОГО М/НАСОСА 17-K-101-PM-102 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.35 |  |  | 0 | 1 | Mpa | [5 empty] | TS-O-03:25/ O1010003_U4:3 | TS-O-03:26/ O1010003_U4:4 |  |  | O1010003:4A/ O1010003_U4:5 | O1010003:4C/ O1010003_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -100768 | 17PT100768 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-GP-VD-BD17917K101004_SH.4 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.14 | 17-MC-DCS-006 | TS-O-03 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010003_U5 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LUBE OIL CIRCUIT PRESSURE | НАГНЕТАНИЕ М/ НАСОСА 17-K-101-P-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.35 |  |  | 0 | 1 | Mpa | [5 empty] | TS-O-03:27/ O1010003_U5:3 | TS-O-03:28/ O1010003_U5:4 |  |  | O1010003:5A/ O1010003_U5:5 | O1010003:5C/ O1010003_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -11100 | 17PT11100 |  | AI-R-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Ultrasonic Flow Transmitter | 4124-XZ-DM-21711101 | DCS_AI_02 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.09 | 17-MC-DCS-009 | TS-H-03 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010102R_U2 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-U-111 Deaerator storage tank | ДАВЛЕНИЕ В ДЕАЭРАТОРЕ 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.05 | 0.18 |  | 0 | 0.35 | MPa | [5 empty] | TS-H-03:17/ O1010102R_U2:3 | TS-H-03:18/ O1010102R_U2:4 |  |  | O1010102R:2A/ O1010102R_U2:5 | O1010102R:2C/ O1010102R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -11100 | 17PY11100 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Guided Wave Radar Level Transmitter | 4124-XZ-DM-21711101 | DCS_AO_02 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.12 | 17-MC-DCS-009 | TS-H-03 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010110R_U7 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 7 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-U-111 Deaerator storage tank | НАКОПИТ БАК ДЕАЭРАТОРА 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-H-03:23/ O1010110R_U7:3 | TS-H-03:24/ O1010110R_U7:4 |  |  | O1010110R:7A/ O1010110R_U7:5 | O1010110R:7C/ O1010110R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -11101 | 17PT11101 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-002FL11 | 12 Pair | Pr.05 | 17-MC-DCS-009 | TS-G-02 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U7 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | DM Water to 17-U-111 | ДЕМ ВОДА В 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.6 |  |  | 0 | 2 | MPa | [5 empty] | TS-G-02:9/ O1010011_U7:3 | TS-G-02:10/ O1010011_U7:4 |  |  | O1010011:7A/ O1010011_U7:5 | O1010011:7C/ O1010011_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -11110 | 17PT11110 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-002FL11 | 12 Pair | Pr.06 | 17-MC-DCS-009 | TS-G-02 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U8 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-U-111 Deaerator storage tank | ДАВЛЕНИЕ В ДЕАЭРАТОРЕ 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.18 |  | 0 | 0.3 | MPa | [5 empty] | TS-G-02:11/ O1010011_U8:3 | TS-G-02:12/ O1010011_U8:4 |  |  | O1010011:8A/ O1010011_U8:5 | O1010011:8C/ O1010011_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -11200 | 17PT11200 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | DP Flow Transmitter | 4124-XZ-DM-21711201 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.10 | 17-MC-DCS-009 | TS-H-03 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U4 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Utility BFW Pump P-111A/B Discharge Line | НАГНЕТАНИЕ 17-P-111-A/B | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5.6 |  |  | 0 | 10 | MPa | [5 empty] | TS-H-03:19/ O1011006_U4:3 | TS-H-03:20/ O1011006_U4:4 |  |  | O1011006:4A/ O1011006_U4:5 | O1011006:4C/ O1011006_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.12 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 08.04.25 сигнал 17PT11287 исключен по TQ-132 | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010100R_U6 | HD5542 | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 6 | AI713-H11 | 16 |  |  | демонтировать провода от клеммной группы TS-Q-01 клеммы 1,2 до барьера демонтировать клеммную группу TS-Q-01 | DCS AMMONIA-UTILITIES | [25 empty] | O1010100R:6A/ O1010100R_U6:5 | O1010100R:6C/ O1010100R_U6:6 | [6 empty] | 6A | 6C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -11301 | 17PT11301 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21711301 | DCS_AI_02 | Field |  | 17-C-AD-I-002FL11 | 12 Pair | Pr.07 | 17-MC-DCS-009 | TS-G-02 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010102R_U13 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From steam turbine of the Boiler supply fan | ПАР НД ОТ 17-L-111-STK-101A | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.45 |  | 0 | 0.6 | MPa | [5 empty] | TS-G-02:13/ O1010102R_U13:3 | TS-G-02:14/ O1010102R_U13:4 |  |  | O1010102R:13A/ O1010102R_U13:5 | O1010102R:13C/ O1010102R_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -11301 | 17PY11301 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | DP Flow Transmitter | 4124-XZ-DM-21711301 | DCS_AO_02 | Field |  | 17-C-AD-I-003FL11 | 12 Pair | Pr.02 | 17-MC-DCS-009 | TS-G-03 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010110R_U3 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 3 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From steam turbine of the Boiler supply fan | ОТ ТУРБИНЫ ВЕНТИЛЯТОРА КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-03:3/ O1010110R_U3:3 | TS-G-03:4/ O1010110R_U3:4 |  |  | O1010110R:3A/ O1010110R_U3:5 | O1010110R:3C/ O1010110R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -11302 | 17PT11302 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter (Pressure) | 4124-XZ-DM-21711301 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.08 | 17-MC-DCS-006 | TS-R-05 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U8 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CEMS for Star-Up-Boiler 17-L-111 | ДАВЛЕНИЕ ДЫМОВЫХ ГАЗОВ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | CEMS |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 99 | 103 |  | 0 | 110 | kPa | [5 empty] | TS-R-05:15/ O1010007_U8:3 | TS-R-05:16/ O1010007_U8:4 |  |  | O1010007:8A/ O1010007_U8:5 | O1010007:8C/ O1010007_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -11305 | 17PT11305 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21711301 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11 | 12 Pair | Pr.07 | 17-MC-DCS-006 | TS-O-04 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010003_U9 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | N2 to Startup Boiler | АЗОТ В ПАР БАРАБАН КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.4 |  |  | 0 | 1.5 | MPa | [5 empty] | TS-O-04:13/ O1010003_U9:3 | TS-O-04:14/ O1010003_U9:4 |  |  | O1010003:9A/ O1010003_U9:5 | O1010003:9C/ O1010003_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -113500 | 17PT113500 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.06 | 17-MC-DCS-006 | TS-O-05 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U2 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | FROM FW PUMPS 17-P-111A/B | ПИТ ВОДА ОТ НАСОСОВ P-111A/B | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 10 | МPa | [5 empty] | TS-O-05:11/ O1010014R_U2:3 | TS-O-05:12/ O1010014R_U2:4 |  |  | O1010014R:2A/ O1010014R_U2:5 | O1010014R:2C/ O1010014R_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -113505 | 17PT113505 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.07 | 17-MC-DCS-006 | TS-O-05 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010003_U14 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | ПАР СД ОТ КОТЛА В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 6 | MPa | [5 empty] | TS-O-05:13/ O1010003_U14:3 | TS-O-05:14/ O1010003_U14:4 |  |  | O1010003:14A/ O1010003_U14:5 | O1010003:14C/ O1010003_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -113505 | 17PY113505 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.16 | 17-MC-DCS-008 | TS-P-02 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010108R_U9 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 9 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | ПАР СД В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-02:31/ O1010108R_U9:3 | TS-P-02:32/ O1010108R_U9:4 |  |  | O1010108R:9A/ O1010108R_U9:5 | O1010108R:9C/ O1010108R_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -113507 | 17PT113507 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.08 | 17-MC-DCS-006 | TS-O-05 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010003_U15 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM DRUM LEVEL 17-L-111-V-111 | ДАВЛЕНИЕ В БАРАБАНЕ ПАРА КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 6 | MPa | [5 empty] | TS-O-05:15/ O1010003_U15:3 | TS-O-05:16/ O1010003_U15:4 |  |  | O1010003:15A/ O1010003_U15:5 | O1010003:15C/ O1010003_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -113522 | 17PT113522 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.02 | 17-MC-DCS-008 | TS-P-02 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010009_U8 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | AIR DUCT PRESSURE | ВОЗДУХ НА ГОРЕНИЕ ПУСКОВОГО КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 7.8 | kPa | [5 empty] | TS-P-02:3/ O1010009_U8:3 | TS-P-02:4/ O1010009_U8:4 |  |  | O1010009:8A/ O1010009_U8:5 | O1010009:8C/ O1010009_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -113526 | 17PT113526 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.03 | 17-MC-DCS-008 | TS-P-02 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010009_U9 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CASING PRESSURE U/S ECO | КОНВЕКЦ ЗОНА КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1.7 | kPa | [5 empty] | TS-P-02:5/ O1010009_U9:3 | TS-P-02:6/ O1010009_U9:4 |  |  | O1010009:9A/ O1010009_U9:5 | O1010009:9C/ O1010009_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -113527 | 17PT113527 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.07 | 17-MC-DCS-008 | TS-P-02 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010010_U4 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CASING PRESSURE D/S ECO | КОНВЕКЦ ЗОНА КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 0.39 | kPa | [5 empty] | TS-P-02:13/ O1010010_U4:3 | TS-P-02:14/ O1010010_U4:4 |  |  | O1010010:4A/ O1010010_U4:5 | O1010010:4C/ O1010010_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -113803 | 17PT113803 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Position Closed Proximity Switch | 4124-FB-VD-BD00317L11111372_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-I-001FL11-L111 | 24 Pair | Pr.05 | 17-MC-DCS-009 | TS-H-04 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010102R_U8 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO ATMOSPHERE | ТГ НА ОСНОВНЫЕ ГОРЕЛКИ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 0.6 | MPa | [5 empty] | TS-H-04:9/ O1010102R_U8:3 | TS-H-04:10/ O1010102R_U8:4 |  |  | O1010102R:8A/ O1010102R_U8:5 | O1010102R:8C/ O1010102R_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -113804 | 17PT113804 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Low Flow Switch (Flow) | 4124-FB-VD-BD00317L11111372_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-I-001FL11-L111 | 24 Pair | Pr.08 | 17-MC-DCS-009 | TS-H-04 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010102R_U9 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO ATMOSPHERE | ТГ НА ОСНОВНЫЕ ГОРЕЛКИ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 0.15 | MPa | [5 empty] | TS-H-04:15/ O1010102R_U9:3 | TS-H-04:16/ O1010102R_U9:4 |  |  | O1010102R:9A/ O1010102R_U9:5 | O1010102R:9C/ O1010102R_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -113804 | 17PY113804 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FB-VD-BD00317L11111372_SH.1 | DCS_AO_02 | Field |  | 17-C-AD-I-001FL11-L111 | 24 Pair | Pr.12 | 17-MC-DCS-009 | TS-H-04 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010110R_U12 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 12 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO ATMOSPHERE | В АТМОСФЕРУ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-H-04:23/ O1010110R_U12:3 | TS-H-04:24/ O1010110R_U12:4 |  |  | O1010110R:12A/ O1010110R_U12:5 | O1010110R:12C/ O1010110R_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -113852 | 17PT113852 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-FB-VD-BD00317L11111372_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11-L111 | 24 Pair | Pr.09 | 17-MC-DCS-009 | TS-H-04 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U7 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | FUEL GAS FLOW | ТГ НА ПИЛОТНЫЕ ГОРЕЛКИ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 0.06 | MPa | [5 empty] | TS-H-04:17/ O1011006_U7:3 | TS-H-04:18/ O1011006_U7:4 |  |  | O1011006:7A/ O1011006_U7:5 | O1011006:7C/ O1011006_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -11801 | 17PT11801 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21711801 | DCS_AI_02 | Field |  | 17-C-AD-I-003FL11 | 12 Pair | Pr.01 | 17-MC-DCS-009 | TS-G-03 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010102R_U14 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Fuel gas to Distribution | ТОПЛ ГАЗ НА ГОРЕЛКИ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.42 | 0.58 |  | 0 | 0.8 | MPa | [5 empty] | TS-G-03:1/ O1010102R_U14:3 | TS-G-03:2/ O1010102R_U14:4 |  |  | O1010102R:14A/ O1010102R_U14:5 | O1010102R:14C/ O1010102R_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -11801 | 17PY11801B |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21711801 | DCS_AO_02 | Field |  | 17-C-AD-I-003FL11 | 12 Pair | Pr.04 | 17-MC-DCS-009 | TS-G-03 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010110R_U10 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 10 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Fuel gas to Distribution | ТОПЛИВНЫЙ ГАЗ В СЕТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-03:7/ O1010110R_U10:3 | TS-G-03:8/ O1010110R_U10:4 |  |  | O1010110R:10A/ O1010110R_U10:5 | O1010110R:10C/ O1010110R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -11801 | 17PY11801A |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21711801 | DCS_AO_02 | Field |  | 17-C-AD-I-003FL11 | 12 Pair | Pr.03 | 17-MC-DCS-009 | TS-G-03 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010110R_U16 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 16 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Fuel gas to Distribution | ТОПЛИВНЫЙ ГАЗ В СЕТЬ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-03:5/ O1010110R_U16:3 | TS-G-03:6/ O1010110R_U16:4 |  |  | O1010110R:16A/ O1010110R_U16:5 | O1010110R:16C/ O1010110R_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -11803 | 17PT11803 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21711801 | DCS_AI_02 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.11 | 17-MC-DCS-009 | TS-H-03 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010102R_U3 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Fuel gas to Distribution | ТОПЛ ГАЗ НА ГОРЕЛКИ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 1 | MPa | [5 empty] | TS-H-03:21/ O1010102R_U3:3 | TS-H-03:22/ O1010102R_U3:4 |  |  | O1010102R:3A/ O1010102R_U3:5 | O1010102R:3C/ O1010102R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -13007 | 17PT13007 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21713001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.10 | 17-MC-DCS-006 | TS-O-02 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011000_U2 | HD5542 | O1011000 | TUA711-AIO16 | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131A Discharge | P-131A НАСОС ВОДЫ АВАР ДУШ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.44 |  |  | 0 | 0.9 | MPa | [5 empty] | TS-O-02:19/ O1011000_U2:3 | TS-O-02:20/ O1011000_U2:4 |  |  | O1011000:2A/ O1011000_U2:5 | O1011000:2C/ O1011000_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -13008 | 17PT13008 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21713001 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.15 | 17-MC-DCS-008 | TS-P-01 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U15 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131B Discharge | P-131В НАСОС ВОДЫ АВАР ДУШ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.44 |  |  | 0 | 0.9 | MPa | [5 empty] | TS-P-01:29/ O1011003_U15:3 | TS-P-01:30/ O1011003_U15:4 |  |  | O1011003:15A/ O1011003_U15:5 | O1011003:15C/ O1011003_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -13009 | 17PT13009 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21713001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.11 | 17-MC-DCS-006 | TS-O-02 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011000_U3 | HD5542 | O1011000 | TUA711-AIO16 | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131C Discharge | P-131С НАСОС ВОДЫ АВАР ДУШ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.44 |  |  | 0 | 0.9 | MPa | [5 empty] | TS-O-02:21/ O1011000_U3:3 | TS-O-02:22/ O1011000_U3:4 |  |  | O1011000:3A/ O1011000_U3:5 | O1011000:3C/ O1011000_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -13010 | 17PT13010 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21713001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.12 | 17-MC-DCS-006 | TS-O-02 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011000_U4 | HD5542 | O1011000 | TUA711-AIO16 | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Safety Shower Pump 17-P-131A/B/C Trip | P-131A/B/C НАСОСЫ ВОДЫ АВАР ДУШ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.44 | 0.55 |  | 0 | 0.9 | MPa | [5 empty] | TS-O-02:23/ O1011000_U4:3 | TS-O-02:24/ O1011000_U4:4 |  |  | O1011000:4A/ O1011000_U4:5 | O1011000:4C/ O1011000_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -17105 | 17PT17105 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21717101 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.06 | 17-MC-DCS-008 | TS-O-02 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U4 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-171 Glycol water expansion vessel | РАСШ БАК Р-РА ГЛИКОЛЯ V-171 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.3 | 0.5 |  | 0 | 0.8 | MPa | [5 empty] | TS-O-02:11/ O1011010R_U4:3 | TS-O-02:12/ O1011010R_U4:4 |  |  | O1011010R:4A/ O1011010R_U4:5 | O1011010R:4C/ O1011010R_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -17105 | 17PY17105A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21717101 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.09 | 17-MC-DCS-008 | TS-O-02 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U4 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 4 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-171 Glycol water expansion vessel | РАСШИР БАК ВОДНО-ГЛИКОЛ 17V171 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-02:17/ O1011014R_U4:3 | TS-O-02:18/ O1011014R_U4:4 |  |  | O1011014R:4A/ O1011014R_U4:5 | O1011014R:4C/ O1011014R_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -17105 | 17PY17105B |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21717101 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.10 | 17-MC-DCS-008 | TS-O-02 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U5 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 5 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-171 Glycol water expansion vessel | РАСШИР БАК ВОДНО-ГЛИКОЛ 17V171 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-02:19/ O1011014R_U5:3 | TS-O-02:20/ O1011014R_U5:4 |  |  | O1011014R:5A/ O1011014R_U5:5 | O1011014R:5C/ O1011014R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -17106 | 17PT17106 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21717101 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.07 | 17-MC-DCS-008 | TS-O-02 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011001_U6 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-171 Glycol water expansion vessel | РАСШ БАК Р-РА ГЛИКОЛЯ V-171 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 0.3 | 0.5 |  | 0 | 0.8 | MPa | [5 empty] | TS-O-02:13/ O1011001_U6:3 | TS-O-02:14/ O1011001_U6:4 |  |  | O1011001:6A/ O1011001_U6:5 | O1011001:6C/ O1011001_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-P -17120 | 17PY17120 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21131004 | DCS_AO_02 | Field |  | 17-PY-17120 | 01 Pair | Pr.01 | 17-MC-DCS-009 | TS-H-02 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A | O1010112R_U1 | HD5546 | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 1 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Glycol Water supply to 17-E-171 | ТЕПЛООБМ ВОД-ГЛИКОЛИЕВОЙ СМЕСИ | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-H-02:1/ O1010112R_U1:3 | TS-H-02:2/ O1010112R_U1:4 |  |  | O1010112R:1A/ O1010112R_U1:5 | O1010112R:1C/ O1010112R_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P -17120 | 17PT17120 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-XZ-DM-21717101 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.08 | 17-MC-DCS-008 | TS-O-02 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U5 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Glycol Water supply to 17-E-171 | НАГНЕТАНИЕ P-171-A/B | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 1 | 1.4 |  | 0 | 2 | MPa | [5 empty] | TS-O-02:15/ O1011010R_U5:3 | TS-O-02:16/ O1011010R_U5:4 |  |  | O1011010R:5A/ O1011010R_U5:5 | O1011010R:5C/ O1011010R_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P-2001 | 17PT2001 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Smart Positioner |  | DCS_AI_01 | Field |  | 17-С-AD-I-1-FL90 | 15 Pair | Pr.04 | 17-MC-DCS-009 | TS-H-05 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A | O1011005_U4 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | HPP Nitrogen Pressure in the Pipeline from Ammonia-2 to Ammonia-1 | АЗОТ СВД ОТ АММИАКА-2 НА АММИАК-1 | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 10 | MPa | [5 empty] | TS-H-05:7/ O1011005_U4:3 | TS-H-05:8/ O1011005_U4:4 |  |  | O1011005:4A/ O1011005_U4:5 | O1011005:4C/ O1011005_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P-2002 | 17PT2002 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Smart Positioner |  | DCS_AI_01 | Field |  | 17-С-AD-I-1-FL90 | 15 Pair | Pr.05 | 17-MC-DCS-009 | TS-H-05 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A | O1011005_U5 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | HHP Nitrogen Pressure in the Pipeline from Ammonia-2 to Urea | АЗОТ СВД ОТ АММИАКА-2 НА КАРБАМИД | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 10 | MPa | [5 empty] | TS-H-05:9/ O1011005_U5:3 | TS-H-05:10/ O1011005_U5:4 |  |  | O1011005:5A/ O1011005_U5:5 | O1011005:5C/ O1011005_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-P-2003 | 17PT2003 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | I/P Converter |  | DCS_AI_01 | Field |  | 17-С-AD-I-1-FL90 | 15 Pair | Pr.06 | 17-MC-DCS-009 | TS-H-05 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A | O1011005_U6 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP Carbon Dioxide Pressure in the Ammonia-1 and 2 Pipeline to Urea | СО2 НД ОТ АММИАКА-2 НА КАРБАМИД | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 0.4 | MPa | [5 empty] | TS-H-05:11/ O1011005_U6:3 | TS-H-05:12/ O1011005_U6:4 |  |  | O1011005:6A/ O1011005_U6:5 | O1011005:6C/ O1011005_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-020202 -A | 17PDT020202A |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.06 | 17-MC-DCS-008 | TS-O-01 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011002_U4 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across SAC Cationic Exchanger | КАТИОНИТ S-021A | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.08 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-01:11/ O1011002_U4:3 | TS-O-01:12/ O1011002_U4:4 |  |  | O1011002:4A/ O1011002_U4:5 | O1011002:4C/ O1011002_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-020202 -B | 17PDT020202B |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.11 | 17-MC-DCS-008 | TS-O-01 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U2 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across SAC Cationic Exchanger | КАТИОНИТ S-021В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.08 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-01:21/ O1011003_U2:3 | TS-O-01:22/ O1011003_U2:4 |  |  | O1011003:2A/ O1011003_U2:5 | O1011003:2C/ O1011003_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-020202 -C | 17PDT020202C |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.16 | 17-MC-DCS-008 | TS-O-01 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U5 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across SAC Cationic Exchanger | КАТИОНИТ S-021С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.08 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-01:31/ O1011003_U5:3 | TS-O-01:32/ O1011003_U5:4 |  |  | O1011003:5A/ O1011003_U5:5 | O1011003:5C/ O1011003_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-020203 -A | 17PDT020203A |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.07 | 17-MC-DCS-008 | TS-O-01 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011002_U5 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Cationic trap | ВЫХОД ИЗ КАТИОНИТА S-021A | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.1 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-01:13/ O1011002_U5:3 | TS-O-01:14/ O1011002_U5:4 |  |  | O1011002:5A/ O1011002_U5:5 | O1011002:5C/ O1011002_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-020203 -B | 17PDT020203B |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.12 | 17-MC-DCS-008 | TS-O-01 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U3 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Cationic trap | ВЫХОД ИЗ КАТИОНИТА S-021В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.1 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-01:23/ O1011003_U3:3 | TS-O-01:24/ O1011003_U3:4 |  |  | O1011003:3A/ O1011003_U3:5 | O1011003:3C/ O1011003_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-020203 -C | 17PDT020203C |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL03-L022 | 24 Pair | Pr.17 | 17-MC-DCS-008 | TS-O-01 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U6 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Cationic trap | ВЫХОД ИЗ КАТИОНИТА S-021С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.1 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-01:33/ O1011003_U6:3 | TS-O-01:34/ O1011003_U6:4 |  |  | O1011003:6A/ O1011003_U6:5 | O1011003:6C/ O1011003_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-020206 -A | 17PDT020206A |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.05 | 17-MC-DCS-008 | TS-O-03 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011002_U7 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Mixed Bed | ФСД S-022А | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.08 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-03:9/ O1011002_U7:3 | TS-O-03:10/ O1011002_U7:4 |  |  | O1011002:7A/ O1011002_U7:5 | O1011002:7C/ O1011002_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-020206 -B | 17PDT020206B |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.10 | 17-MC-DCS-008 | TS-O-03 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U8 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Mixed Bed | ФСД S-022В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.08 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-03:19/ O1011003_U8:3 | TS-O-03:20/ O1011003_U8:4 |  |  | O1011003:8A/ O1011003_U8:5 | O1011003:8C/ O1011003_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-020206 -C | 17PDT020206C |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL03-L022 | 24 Pair | Pr.15 | 17-MC-DCS-008 | TS-O-03 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011003_U11 | HD5542 | O1011003 | TUA711-AIO16 | 17-SC-DCS-002/O1011003/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011003 | 4 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Mixed Bed | ФСД S-022С | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.08 |  | 0 | 0.2 | MPa | [5 empty] | TS-O-03:29/ O1011003_U11:3 | TS-O-03:30/ O1011003_U11:4 |  |  | O1011003:11A/ O1011003_U11:5 | O1011003:11C/ O1011003_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-070173 | 17PDT070173 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-GF-VD-BD17717L072003 | DCS_AI_01 | Field |  | 17-PDT-070173 | 01 Pair | Pr.01 | 17-MC-DCS-006 | TS-P-02 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A | O1010006_U15 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | PRESSURE ROTARY FILTER 17-L-072B | ФИЛЬТР ОВ 17-L-072B | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.05 |  | 0 | 0.1 | Mpa | [5 empty] | TS-P-02:1/ O1010006_U15:3 | TS-P-02:2/ O1010006_U15:4 |  |  | O1010006:15A/ O1010006_U15:5 | O1010006:15C/ O1010006_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-070174 | 17PDT070174 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-GF-VD-BD17717L072003 | DCS_AI_01 | Field |  | 17-PDT-070174 | 01 Pair | Pr.01 | 17-MC-DCS-006 | TS-P-01 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A | O1010007_U11 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | PRESSURE ROTARY FILTER 17-L-072A | ФИЛЬТР ОВ 17-L-072А | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.05 |  | 0 | 0.1 | Mpa | [5 empty] | TS-P-01:1/ O1010007_U11:3 | TS-P-01:2/ O1010007_U11:4 |  |  | O1010007:11A/ O1010007_U11:5 | O1010007:11C/ O1010007_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-090301 | 17PDT090301 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | H2O Analyzer Transmitter | 4124-GY-VD-BD17517L091091_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-I-004FL10-L091 | 12 Pair | Pr.01 | 17-MC-DCS-009 | TS-G-04 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U15 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across PRE-FILTER | ФИЛЬТР ДО ОСУШИТЕЛЕЙ ВОЗДУХА КИП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 30 |  | 0 | 50 | KPa | [5 empty] | TS-G-04:1/ O1010011_U15:3 | TS-G-04:2/ O1010011_U15:4 |  |  | O1010011:15A/ O1010011_U15:5 | O1010011:15C/ O1010011_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-090302 | 17PDT090302 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-GY-VD-BD17517L091091_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-I-004FL10-L091 | 12 Pair | Pr.02 | 17-MC-DCS-009 | TS-G-04 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011006_U9 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Atmospheric Air Trains A and B | ОСУШИТЕЛИ ВОЗДУХА КИП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 30 |  | 0 | 50 | KPa | [5 empty] | TS-G-04:3/ O1011006_U9:3 | TS-G-04:4/ O1011006_U9:4 |  |  | O1011006:9A/ O1011006_U9:5 | O1011006:9C/ O1011006_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-090303 | 17PDT090303 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Guided Wave Radar Level Transmitter | 4124-GY-VD-BD17517L091091_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-I-004FL10-L091 | 12 Pair | Pr.03 | 17-MC-DCS-009 | TS-G-04 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011006_U14 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Across Filter | ФИЛЬТРА ПОСЛЕ ОСУШИТЕЛЕЙ ВОЗДУХА КИП | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 30 |  | 0 | 50 | KPa | [5 empty] | TS-G-04:5/ O1011006_U14:3 | TS-G-04:6/ O1011006_U14:4 |  |  | O1011006:14A/ O1011006_U14:5 | O1011006:14C/ O1011006_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-100744 | 17PDT100744 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-GP-VD-BD17917K101004_SH.4 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.09 | 17-MC-DCS-006 | TS-O-03 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U16 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LUBE OIL CIRCUIT CHANGE OVER FILTER | МАСЛОФИЛЬТР 17-К-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.05 |  | 0 | 0.16 | Mpa | [5 empty] | TS-O-03:17/ O1010002_U16:3 | TS-O-03:18/ O1010002_U16:4 |  |  | O1010002:16A/ O1010002_U16:5 | O1010002:16C/ O1010002_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-PD-11215 | 17PDT11215 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Differential Pressure Transmitter | 4124-XZ-DM-21711201 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11 | 12 Pair | Pr.04 | 17-MC-DCS-006 | TS-O-04 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010003_U7 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Utility BFW Pump P-111A Suction Strainer | ФИЛЬТР ВСАСА 17-P-111-A | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.015 |  | 0 | 10 | MPa | [5 empty] | TS-O-04:7/ O1010003_U7:3 | TS-O-04:8/ O1010003_U7:4 |  |  | O1010003:7A/ O1010003_U7:5 | O1010003:7C/ O1010003_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-PD-11216 | 17PDT11216 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Differential Pressure Transmitter | 4124-XZ-DM-21711201 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11 | 12 Pair | Pr.05 | 17-MC-DCS-006 | TS-O-04 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010003_U8 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Utility BFW Pump P-111B Suction Strainer | ФИЛЬТР ВСАСА 17-P-111-B | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 0.015 |  | 0 | 10 | MPa | [5 empty] | TS-O-04:9/ O1010003_U8:3 | TS-O-04:10/ O1010003_U8:4 |  |  | O1010003:8A/ O1010003_U8:5 | O1010003:8C/ O1010003_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-113705 | 17PDT113705 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Differential Pressure Transmitter | 4124-FB-VD-BD00317L11111309 | DCS_AI_01 | Field |  | 17-C-AD-N-702FL11-L111 | 06 Pair | Pr.02 | 17-MC-DCS-006 | TS-Q-06 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010006_U12 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Oil Tank 17-L-111-S-111A & 17-L-111-S-111B | ФИЛЬТР СМАЗОЧНОГО МАСЛА ДУТ ВЕНТ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 0.01 | Mpa | [5 empty] | TS-Q-06:3/ O1010006_U12:3 | TS-Q-06:4/ O1010006_U12:4 |  |  | O1010006:12A/ O1010006_U12:5 | O1010006:12C/ O1010006_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-PD-113801 | 17PDT113801 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Pressure Transmitter | 4124-FB-VD-BD00317L11111372_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11-L111 | 24 Pair | Pr.04 | 17-MC-DCS-009 | TS-H-04 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U6 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO ATMOSPHERE | ФИЛЬТРА ТГ ПУСКОВОГО КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 0.1 | Mpa | [5 empty] | TS-H-04:7/ O1011006_U6:3 | TS-H-04:8/ O1011006_U6:4 |  |  | O1011006:6A/ O1011006_U6:5 | O1011006:6C/ O1011006_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.12 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 08.04.25 сигнал 17SZI11281AX исключен по TQ-132 | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010000_U10 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 10 | AI713-H11 | 16 |  |  | демонтировать провода от клеммной группы TS-R-03 клеммы 1,2 до барьера | DCS AMMONIA-UTILITIES | [25 empty] | O1010000:10A/ O1010000_U10:5 | O1010000:10C/ O1010000_U10:6 | [6 empty] | 10A | 10C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.12 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 08.04.25 сигнал 17SZI11281BX исключен по TQ-132 | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010000_U11 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 11 | AI713-H11 | 16 |  |  | демонтировать провода от клеммной группы TS-R-03 клеммы 3, 4 до барьера | DCS AMMONIA-UTILITIES | [25 empty] | O1010000:11A/ O1010000_U11:5 | O1010000:11C/ O1010000_U11:6 | [6 empty] | 11A | 11C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.12 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 08.04.25 сигнал 17SZI11281CX исключен по TQ-132 | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010000_U12 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 12 | AI713-H11 | 16 |  |  | демонтировать провода от клеммной группы TS-R-03 клеммы 5, 6 до барьера | DCS AMMONIA-UTILITIES | [25 empty] | O1010000:12A/ O1010000_U12:5 | O1010000:12C/ O1010000_U12:6 | [6 empty] | 12A | 12C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-S -113930 | 17SZI113930AX |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Speed Indication | 4124-FB-VD-BD00317L11111310 | DCS_AI_01 | RR-AM |  | 17-I-AD-N-001BL02 | 12 Pair | Pr.04 | 17-MC-DCS-006 | TS-R-03 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010000_U13 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | SPEED DETECTION | ТУРБИНА ДУТЬЕВОГО ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | OST |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0.5 | 25000 | об/мин | [5 empty] | TS-R-03:7/ O1010000_U13:3 | TS-R-03:8/ O1010000_U13:4 |  |  | O1010000:13A/ O1010000_U13:5 | O1010000:13C/ O1010000_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-S -113930 | 17SZI113930BX |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Speed Indication | 4124-FB-VD-BD00317L11111310 | DCS_AI_01 | RR-AM |  | 17-I-AD-N-001BL02 | 12 Pair | Pr.05 | 17-MC-DCS-006 | TS-R-03 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010000_U14 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | SPEED DETECTION | ТУРБИНА ДУТЬЕВОГО ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | OST |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0.5 | 25000 | об/мин | [5 empty] | TS-R-03:9/ O1010000_U14:3 | TS-R-03:10/ O1010000_U14:4 |  |  | O1010000:14A/ O1010000_U14:5 | O1010000:14C/ O1010000_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-S -113930 | 17SZI113930CX |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Speed Indication | 4124-FB-VD-BD00317L11111310 | DCS_AI_01 | RR-AM |  | 17-I-AD-N-001BL02 | 12 Pair | Pr.06 | 17-MC-DCS-006 | TS-R-03 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010000_U15 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | SPEED DETECTION | ТУРБИНА ДУТЬЕВОГО ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | OST |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0.5 | 25000 | об/мин | [5 empty] | TS-R-03:11/ O1010000_U15:3 | TS-R-03:12/ O1010000_U15:4 |  |  | O1010000:15A/ O1010000_U15:5 | O1010000:15C/ O1010000_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-S -113932 | 17SV113932 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Globe Control Valve | 4124-FB-VD-BD00317L11111310 | DCS_AO_02 | Field |  | 17-C-AD-N-702FL11-L111 | 06 Pair | Pr.05 | 17-MC-DCS-006 | TS-Q-06 | 9 | 10 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010106R_U11 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 11 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE GOVERNOR VALVE | РЕГУЛ КЛАПАН ПАРОВОЙ ТУРБИНЫ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-06:9/ O1010106R_U11:3 | TS-Q-06:10/ O1010106R_U11:4 |  |  | O1010106R:11A/ O1010106R_U11:5 | O1010106R:11C/ O1010106R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-S -113932 | 17SI113932A |  | AI-R-NIS (PI converter, 3 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Speed Element | 4124-FB-VD-BD00317L11111310 | DCS_PI_01 | Field |  | 17-C-XD-N-707FL11-L111 | 06 Triad | Tr.01 | 17-MC-DCS-007 | TS-F-16 | 1 | 2 | 3 | 18 | AVK 2,5 A, AVK 2,5 A | O1011008R_U1 | GS8555-EX | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE SPEED SENSOR | ТУРБИНА ДУТЬЕВОГО ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-16:1/ O1011008R_U1:13 | TS-F-16:2/ O1011008R_U1:14 | TS-F-16:3/ O1011008R_U1:11 |  | O1011008R:1A/ O1011008R_U1:3 | O1011008R:1C/ O1011008R_U1:4 | [6 empty] | 1A | 1C | 13 | 14 | 11 | 3 | 4 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-S -113932 | 17SI113932B |  | AI-R-NIS (PI converter, 3 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Speed Element | 4124-FB-VD-BD00317L11111310 | DCS_PI_01 | Field |  | 17-C-XD-N-707FL11-L111 | 06 Triad | Tr.02 | 17-MC-DCS-007 | TS-F-16 | 4 | 5 | 6 | 18 | AVK 2,5 A, AVK 2,5 A | O1011008R_U2 | GS8555-EX | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE SPEED SENSOR | ТУРБИНА ДУТЬЕВОГО ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-16:4/ O1011008R_U2:13 | TS-F-16:5/ O1011008R_U2:14 | TS-F-16:6/ O1011008R_U2:11 |  | O1011008R:2A/ O1011008R_U2:3 | O1011008R:2C/ O1011008R_U2:4 | [6 empty] | 2A | 2C | 13 | 14 | 11 | 3 | 4 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -00005 | 17TT00005 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | DP Flow Transmitter | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.14 | 17-MC-DCS-009 | TS-H-03 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U5 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP steam to Dearetor | ПАР НД В ДЕАЭРАТОР | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 250 | °C | [5 empty] | TS-H-03:27/ O1011006_U5:3 | TS-H-03:28/ O1011006_U5:4 |  |  | O1011006:5A/ O1011006_U5:5 | O1011006:5C/ O1011006_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -020200 | 17TT020200A |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_AI_02 | Field |  | 17-C-AD-N-003FL03-L022 | 12 Pair | Pr.01 | 17-MC-DCS-008 | TS-O-06 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011010R_U10 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Water from regeneration pumps | ВОДА НА РЕГЕНЕРАЦИЮ ФСД | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 60 | °C | [5 empty] | TS-O-06:1/ O1011010R_U10:3 | TS-O-06:2/ O1011010R_U10:4 |  |  | O1011010R:10A/ O1011010R_U10:5 | O1011010R:10C/ O1011010R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -020200 | 17TT020200B |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_AI_02 | Field |  | 17-C-AD-N-003FL03-L022 | 12 Pair | Pr.02 | 17-MC-DCS-008 | TS-O-06 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011010R_U11 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Water from regeneration pumps | ВОДА НА РЕГЕНЕРАЦИЮ ФСД | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 60 | °C | [5 empty] | TS-O-06:3/ O1011010R_U11:3 | TS-O-06:4/ O1011010R_U11:4 |  |  | O1011010R:11A/ O1011010R_U11:5 | O1011010R:11C/ O1011010R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -020200 | 17TY0020200 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL03-L022 | 12 Pair | Pr.03 | 17-MC-DCS-008 | TS-O-06 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011014R_U10 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 10 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Steam to NaOH regeneration | ПАР К РЕГЕНЕРАЦИИ NAOH | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-06:5/ O1011014R_U10:3 | TS-O-06:6/ O1011014R_U10:4 |  |  | O1011014R:10A/ O1011014R_U10:5 | O1011014R:10C/ O1011014R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -020201 | 17TT020201 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_AI_01 | Field |  | 17-C-AD-N-005FL03-L022 | 06 Pair | Pr.02 | 17-MC-DCS-008 | TS-O-09 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011004_U8 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | NaOH storage tank | БАК NAOH НА ДЕМ ВОДЕ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 10 | 17 |  | 0 | 60 | °C | [5 empty] | TS-O-09:3/ O1011004_U8:3 | TS-O-09:4/ O1011004_U8:4 |  |  | O1011004:8A/ O1011004_U8:5 | O1011004:8C/ O1011004_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -020202 | 17TT020202 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FY-VD-BD17617L02200002_SH.6 | DCS_AI_01 | Field |  | 17-C-AD-N-005FL03-L022 | 06 Pair | Pr.03 | 17-MC-DCS-008 | TS-O-09 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1011004_U9 | HD5542 | O1011004 | TUA711-AIO16 | 17-SC-DCS-002/O1011004/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011004 | 5 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | NaOH storage tank | БАК NAOH НА ДЕМ ВОДЕ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 10 | 17 |  | 0 | 60 | °C | [5 empty] | TS-O-09:5/ O1011004_U9:3 | TS-O-09:6/ O1011004_U9:4 |  |  | O1011004:9A/ O1011004_U9:5 | O1011004:9C/ O1011004_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -02081 | 17TT02081 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21702020 | DCS_AI_02 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.11 | 17-MC-DCS-006 | TS-Q-05 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U10 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-021 Temperature | БАК НЕКОНДИЦИРННОГО КОНД 17-T-021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 |  |  | -50 | 100 | °C | [5 empty] | TS-Q-05:21/ O1010014R_U10:3 | TS-Q-05:22/ O1010014R_U10:4 |  |  | O1010014R:10A/ O1010014R_U10:5 | O1010014R:10C/ O1010014R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -02081 | 17TY02081 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21702020 | DCS_AO_02 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.16 | 17-MC-DCS-006 | TS-Q-05 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010106R_U9 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 9 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-021 Temperature | ТЕМПЕРАТУРА В БАКЕ 17-T-021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-05:31/ O1010106R_U9:3 | TS-Q-05:32/ O1010106R_U9:4 |  |  | O1010106R:9A/ O1010106R_U9:5 | O1010106R:9C/ O1010106R_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -02087 | 17TT02087 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21702020 | DCS_AI_02 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.12 | 17-MC-DCS-006 | TS-Q-05 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U11 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 17-P-021 discharge to stripper | НАГНЕТ 17-P-021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 65 | 75 |  | -50 | 100 | °C | [5 empty] | TS-Q-05:23/ O1010014R_U11:3 | TS-Q-05:24/ O1010014R_U11:4 |  |  | O1010014R:11A/ O1010014R_U11:5 | O1010014R:11C/ O1010014R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -02087 | 17TY02087 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21702020 | DCS_AO_02 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.17 | 17-MC-DCS-006 | TS-Q-04 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010106R_U7 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 7 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 17-P-021 discharge to stripper | ТЕМПЕРАТУРА НА НАГНЕТАНИИ 17P021 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:33/ O1010106R_U7:3 | TS-Q-04:34/ O1010106R_U7:4 |  |  | O1010106R:7A/ O1010106R_U7:5 | O1010106R:7C/ O1010106R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -03002 | 17TT03002 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21703001 | DCS_AI_02 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.13 | 17-MC-DCS-006 | TS-Q-05 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U12 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-032 Vessel Temp | БАК ДЕМ ВОДЫ 17-T-032 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 50 |  | -50 | 80 | °C | [5 empty] | TS-Q-05:25/ O1010014R_U12:3 | TS-Q-05:26/ O1010014R_U12:4 |  |  | O1010014R:12A/ O1010014R_U12:5 | O1010014R:12C/ O1010014R_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -03002 | 17TY03002 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21703001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.18 | 17-MC-DCS-006 | TS-O-02 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U14 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 14 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-032 Vessel Temp | БАК ДЕМ ВОДЫ 17-T-032 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-02:35/ O1010104R_U14:3 | TS-O-02:36/ O1010104R_U14:4 |  |  | O1010104R:14A/ O1010104R_U14:5 | O1010104R:14C/ O1010104R_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -03007 | 17TT03007 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21703001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.15 | 17-MC-DCS-006 | TS-O-02 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U9 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 17-P-032A/B/C discharge line | НАГНЕТ 17-P-032A/B/C | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 50 |  | -50 | 100 | °C | [5 empty] | TS-O-02:29/ O1010002_U9:3 | TS-O-02:30/ O1010002_U9:4 |  |  | O1010002:9A/ O1010002_U9:5 | O1010002:9C/ O1010002_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -03011 | 17TT03011 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21703006 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.15 | 17-MC-DCS-006 | TS-Q-04 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U7 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 17-17-P-020A/B discharge line | ПАРОВОЙ КОНДЕНСАТ ОТ 17-P-020A/B | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 56 |  | -50 | 120 | °C | [5 empty] | TS-Q-04:29/ O1010005_U7:3 | TS-Q-04:30/ O1010005_U7:4 |  |  | O1010005:7A/ O1010005_U7:5 | O1010005:7C/ O1010005_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -03021 | 17TT03021 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21703004 | DCS_AI_01 | Field |  | 17-C-AD-N-003FL10 | 24 Pair | Pr.16 | 17-MC-DCS-006 | TS-Q-04 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U8 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Process Condensate from 17-P-030 A/B/C | ТЕХНОЛ КОНД ОТ 17-P-030-A/B/C | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 50 |  | -50 | 80 | °C | [5 empty] | TS-Q-04:31/ O1010005_U8:3 | TS-Q-04:32/ O1010005_U8:4 |  |  | O1010005:8A/ O1010005_U8:5 | O1010005:8C/ O1010005_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -03022 | 17TT03022 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21703004 | DCS_AI_02 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.14 | 17-MC-DCS-006 | TS-Q-05 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U13 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-030 Vessel Temp | КОНДЕНСАТ В 17-T-030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 50 |  | -50 | 80 | °C | [5 empty] | TS-Q-05:27/ O1010014R_U13:3 | TS-Q-05:28/ O1010014R_U13:4 |  |  | O1010014R:13A/ O1010014R_U13:5 | O1010014R:13C/ O1010014R_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -03022 | 17TY03022 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21703004 | DCS_AO_02 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.17 | 17-MC-DCS-006 | TS-Q-05 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010106R_U10 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 10 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-030 Vessel Temp | ТЕМПЕРАТУРА КОНДЕНСАТА В 17T030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-05:33/ O1010106R_U10:3 | TS-Q-05:34/ O1010106R_U10:4 |  |  | O1010106R:10A/ O1010106R_U10:5 | O1010106R:10C/ O1010106R_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -03041 | 17TT03041 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21703003 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.16 | 17-MC-DCS-006 | TS-O-02 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010012R_U13 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-031 Vessel Temp | БАК 17-T-031 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 50 |  | -50 | 80 | °C | [5 empty] | TS-O-02:31/ O1010012R_U13:3 | TS-O-02:32/ O1010012R_U13:4 |  |  | O1010012R:13A/ O1010012R_U13:5 | O1010012R:13C/ O1010012R_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -03041 | 17TY03041 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21703003 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.19 | 17-MC-DCS-006 | TS-O-02 | 37 | 38 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010104R_U15 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 15 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-T-031 Vessel Temp | ТЕМПЕРАТУРА ВОЗВР КОНД В 17T031 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-02:37/ O1010104R_U15:3 | TS-O-02:38/ O1010104R_U15:4 |  |  | O1010104R:15A/ O1010104R_U15:5 | O1010104R:15C/ O1010104R_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -03065 | 17TT03065 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21703003 | DCS_AI_01 | Field |  | 17-C-AD-N-004FL10 | 24 Pair | Pr.15 | 17-MC-DCS-006 | TS-Q-05 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010005_U16 | HD5542 | O1010005 | TUA711-AIO16 | 17-SC-DCS-001/O1010005/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010005 | 6 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-031A/B/C discharge to 17-S-022A/B/C | КОНД ОТ 17-Р-031 НА ФСД | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 50 |  | -50 | 80 | °C | [5 empty] | TS-Q-05:29/ O1010005_U16:3 | TS-Q-05:30/ O1010005_U16:4 |  |  | O1010005:16A/ O1010005_U16:5 | O1010005:16C/ O1010005_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -07001 | 17TT07001 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21707001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL07 | 12 Pair | Pr.08 | 17-MC-DCS-006 | TS-O-01 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010001_U4 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CWR from distribution header | ВОЗВРАТ ОВ НА ГРАДИРНЮ | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 38 |  | -50 | 50 | °C | [5 empty] | TS-O-01:15/ O1010001_U4:3 | TS-O-01:16/ O1010001_U4:4 |  |  | O1010001:4A/ O1010001_U4:5 | O1010001:4C/ O1010001_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -07032 | 17TT07032 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21707003 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL07 | 12 Pair | Pr.09 | 17-MC-DCS-006 | TS-O-01 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010012R_U9 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | To Distribution header CWS | ОВ НА ФИЛЬТРАЦИЮ L-072А/В | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 16 | 28 |  | -50 | 50 | °C | [5 empty] | TS-O-01:17/ O1010012R_U9:3 | TS-O-01:18/ O1010012R_U9:4 |  |  | O1010012R:9A/ O1010012R_U9:5 | O1010012R:9C/ O1010012R_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -07043 | 17TT07043A |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21707007 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.14 | 17-MC-DCS-006 | TS-Q-03 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U9 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From 17-A-002 to Emergency cooling water | АВАР ОХЛ ВОДА В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 12 | 28 |  | -50 | 50 | °C | [5 empty] | TS-Q-03:27/ O1010006_U9:3 | TS-Q-03:28/ O1010006_U9:4 |  |  | O1010006:9A/ O1010006_U9:5 | O1010006:9C/ O1010006_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -07043 | 17TT07043B |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21707007 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL07 | 24 Pair | Pr.15 | 17-MC-DCS-006 | TS-Q-03 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U10 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From 17-A-002 to Emergency cooling water | АВАР ОХЛ ВОДА В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 12 | 28 |  | -50 | 50 | °C | [5 empty] | TS-Q-03:29/ O1010006_U10:3 | TS-Q-03:30/ O1010006_U10:4 |  |  | O1010006:10A/ O1010006_U10:5 | O1010006:10C/ O1010006_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -090101 | 17TY090135 |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-GY-VD-BD17517L091090_SH.1 | DCS_AO_02 | Field |  | 17-C-AP-I-002FL10-L091 | 06 Pair | Pr.05 | 17-MC-DCS-009 | TS-H-01 | 9 | 10 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010110R_U4 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 4 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From GWS Circuit | ИЗ КОНТУРА ОБОРОТНОЙ ОХЛ ВОДЫ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | % | [5 empty] | TS-H-01:9/ O1010110R_U4:3 | TS-H-01:10/ O1010110R_U4:4 |  |  | O1010110R:4A/ O1010110R_U4:5 | O1010110R:4C/ O1010110R_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -10003 | 17TT10003 |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21710001 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.09 | 17-MC-DCS-008 | TS-P-01 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010009_U5 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | АЗОТ ИЗ 17-V-106 В СЕТЬ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 50 | °C | [5 empty] | TS-P-01:17/ O1010009_U5:3 | TS-P-01:18/ O1010009_U5:4 |  |  | O1010009:5A/ O1010009_U5:5 | O1010009:5C/ O1010009_U5:6 | [6 empty] | 5A | 5C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -10006 | 17TT10006 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21710000 | DCS_AI_02 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.10 | 17-MC-DCS-008 | TS-P-01 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010100R_U3 | HD5542 | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP Steam to Header | LS ОТ ТУРБИНЫ АЗОТНОЙ УСТАНОВКИ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 360 | °C | [5 empty] | TS-P-01:19/ O1010100R_U3:3 | TS-P-01:20/ O1010100R_U3:4 |  |  | O1010100R:3A/ O1010100R_U3:5 | O1010100R:3C/ O1010100R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -10006 | 17TY10006A |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21710000 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.13 | 17-MC-DCS-008 | TS-P-01 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010108R_U3 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 3 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP Steam to Header | ПАР НД В КОЛЛЕКТОР | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-01:25/ O1010108R_U3:3 | TS-P-01:26/ O1010108R_U3:4 |  |  | O1010108R:3A/ O1010108R_U3:5 | O1010108R:3C/ O1010108R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -10008 | 17TT10008 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21710000 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.11 | 17-MC-DCS-008 | TS-P-01 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010009_U6 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LP Steam to Header | LS ОТ ТУРБИНЫ АЗОТНОЙ УСТАНОВКИ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 278 |  | -50 | 360 | °C | [5 empty] | TS-P-01:21/ O1010009_U6:3 | TS-P-01:22/ O1010009_U6:4 |  |  | O1010009:6A/ O1010009_U6:5 | O1010009:6C/ O1010009_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -10011 | 17TT10011 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21710001 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL10 | 24 Pair | Pr.12 | 17-MC-DCS-008 | TS-P-01 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010009_U7 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | АЗОТ НД НА К-1 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 25 | 45 |  | -50 | 50 | °C | [5 empty] | TS-P-01:23/ O1010009_U7:3 | TS-P-01:24/ O1010009_U7:4 |  |  | O1010009:7A/ O1010009_U7:5 | O1010009:7C/ O1010009_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -100709 | 17TT100709 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Remote Mounted | 4124-GP-VD-BD17917K101004_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.03 | 17-MC-DCS-006 | TS-O-03 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U12 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 1st STAGE DISHARGE TEMPERATURE | НАГНЕТАНИЕ 1 СТУПЕНИ АЗОТ КОМПР 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 155 |  | 0 | 200 | °C | [5 empty] | TS-O-03:5/ O1010002_U12:3 | TS-O-03:6/ O1010002_U12:4 |  |  | O1010002:12A/ O1010002_U12:5 | O1010002:12C/ O1010002_U12:6 | [6 empty] | 12A | 12C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -100715 | 17TT100715 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Remote Mounted | 4124-GP-VD-BD17917K101004_SH.2 | DCS_AI_01 | LP |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.04 | 17-MC-DCS-006 | TS-O-03 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010000_U7 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 2st STAGE DISHARGE TEMPERATURE | НАГНЕТАНИЕ 2 СТУПЕНИ АЗОТ КОМПР 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 155 |  | 0 | 200 | °C | [5 empty] | TS-O-03:7/ O1010000_U7:3 | TS-O-03:8/ O1010000_U7:4 |  |  | O1010000:7A/ O1010000_U7:5 | O1010000:7C/ O1010000_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -100717 | 17TE100717 |  | AI-RTD-NIS (3 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Element - RTD | 4124-GP-VD-BD17917K101004_SH.3 | DCS_AI_05 | Field |  | 17-C-RD-N-002FL10-K101 | 06 Triad | Tr.05 | 17-MC-DCS-006 | TS-Q-07 | 13 | 14 | 15 | 18 | AVK 2,5 A, AVK 2,5 A, AVK 2,5 A | O1010008_U5 | HD5573 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | MOTOR NDE BEARING TEMPERATURE | ПОДШИПНИК ЭЛ ДВИГАТЕЛЯ 17-KM-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 100 |  | 0 | 150 | °C | [5 empty] | TS-Q-07:13/ O1010008_U5:1 | TS-Q-07:14/ O1010008_U5:3 | TS-Q-07:15/ O1010008_U5:4 |  | O1010008:5A/ O1010008_U5:5 | O1010008:5C/ O1010008_U5:6 | [6 empty] | 5A | 5C | 1 | 3 | 4 | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -100737 | 17TT100737 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Remote Mounted | 4124-GP-VD-BD17917K101004_SH.4 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.07 | 17-MC-DCS-006 | TS-O-03 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U14 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CRANKCASE LUBE OIL TEMPERATURE | МАСЛОБАК 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 10 | 20 | 70 | 0 | 100 | °C | [5 empty] | TS-O-03:13/ O1010002_U14:3 | TS-O-03:14/ O1010002_U14:4 |  |  | O1010002:14A/ O1010002_U14:5 | O1010002:14C/ O1010002_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -100738 | 17TSHH100738 |  | DI-NIS (VFC) DCS |  | Сигнал | Temperature Switch | 4124-GP-VD-BD17917K101004_SH.4 | DCS_DI_01 | Field |  | 17-C-DD-001-LP001-K101 | 12 Pair | Pr.07 | 17-MC-DCS-007 | TS-F-01 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | CRANKCASE LUBE OIL HEATER TEMPERATURE | ПОДОГРЕВ СМАЗ МАСЛА В КАРТЕРЕ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [5 empty] | 100 | °C | [12 empty] | TS-F-01:13/ O1011113:7A | TS-F-01:14/ O1011113:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -100740 | 17TT100740 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Remote Mounted | 4124-GP-VD-BD17917K101004_SH.4 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.08 | 17-MC-DCS-006 | TS-O-03 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010002_U15 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LUBE OIL CIRCUIT TEMPERATURE | СМАЗОЧНОЕ МАСЛО 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 10 | 70 |  | 0 | 100 | °C | [5 empty] | TS-O-03:15/ O1010002_U15:3 | TS-O-03:16/ O1010002_U15:4 |  |  | O1010002:15A/ O1010002_U15:5 | O1010002:15C/ O1010002_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -100743 | 17TT100743 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Remote Mounted | 4124-GP-VD-BD17917K101004_SH.5 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL10-K101 | 24 Pair | Pr.12 | 17-MC-DCS-006 | TS-O-03 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010003_U3 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | COOLING WATER OUTLET TEMPERATURE | ВЫХОД ОВ ОТ 17-K-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 55 |  | 0 | 100 | °C | [5 empty] | TS-O-03:23/ O1010003_U3:3 | TS-O-03:24/ O1010003_U3:4 |  |  | O1010003:3A/ O1010003_U3:5 | O1010003:3C/ O1010003_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -100763 | 17TE100763A |  | AI-RTD-NIS (3 wire) DCS |  | Сигнал | Temperature Element - RTD | 4124-GP-VD-BD17917K101004_SH.3 | DCS_AI_05 | Field |  | 17-C-RD-N-002FL10-K101 | 06 Triad | Tr.03 | 17-MC-DCS-006 | TS-Q-07 | 7 | 8 | 9 | 18 | AVK 2,5 A, AVK 2,5 A, AVK 2,5 A | O1010008_U3 | HD5573 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | MOTOR WINDING "W" TEMPERATURE | ТЕМП ОБМОТ W ДВИГАТЕЛЯ 17-KM-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 135 |  | 0 | 150 | °C | [5 empty] | TS-Q-07:7/ O1010008_U3:1 | TS-Q-07:8/ O1010008_U3:3 | TS-Q-07:9/ O1010008_U3:4 |  | O1010008:3A/ O1010008_U3:5 | O1010008:3C/ O1010008_U3:6 | [6 empty] | 3A | 3C | 1 | 3 | 4 | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -100764 | 17TE100764A |  | AI-RTD-NIS (3 wire) DCS |  | Сигнал | Temperature Element - RTD | 4124-GP-VD-BD17917K101004_SH.3 | DCS_AI_05 | Field |  | 17-C-RD-N-002FL10-K101 | 06 Triad | Tr.02 | 17-MC-DCS-006 | TS-Q-07 | 4 | 5 | 6 | 18 | AVK 2,5 A, AVK 2,5 A, AVK 2,5 A | O1010008_U2 | HD5573 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | MOTOR WINDING "V" TEMPERATURE | ТЕМП ОБМОТ V ДВИГАТЕЛЯ 17-KM-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 135 |  | 0 | 150 | °C | [5 empty] | TS-Q-07:4/ O1010008_U2:1 | TS-Q-07:5/ O1010008_U2:3 | TS-Q-07:6/ O1010008_U2:4 |  | O1010008:2A/ O1010008_U2:5 | O1010008:2C/ O1010008_U2:6 | [6 empty] | 2A | 2C | 1 | 3 | 4 | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -100765 | 17TE100765A |  | AI-RTD-NIS (3 wire) DCS |  | Сигнал | Temperature Element - RTD | 4124-GP-VD-BD17917K101004_SH.3 | DCS_AI_05 | Field |  | 17-C-RD-N-002FL10-K101 | 06 Triad | Tr.01 | 17-MC-DCS-006 | TS-Q-07 | 1 | 2 | 3 | 18 | AVK 2,5 A, AVK 2,5 A, AVK 2,5 A | O1010008_U1 | HD5573 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | MOTOR WINDING "U" TEMPERATURE | ТЕМП ОБМОТ U ДВИГАТЕЛЯ 17-KM-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 135 |  | 0 | 150 | °C | [5 empty] | TS-Q-07:1/ O1010008_U1:1 | TS-Q-07:2/ O1010008_U1:3 | TS-Q-07:3/ O1010008_U1:4 |  | O1010008:1A/ O1010008_U1:5 | O1010008:1C/ O1010008_U1:6 | [6 empty] | 1A | 1C | 1 | 3 | 4 | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -100766 | 17TE100766 |  | AI-RTD-NIS (3 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Element - RTD | 4124-GP-VD-BD17917K101004_SH.3 | DCS_AI_05 | Field |  | 17-C-RD-N-002FL10-K101 | 06 Triad | Tr.04 | 17-MC-DCS-006 | TS-Q-07 | 10 | 11 | 12 | 18 | AVK 2,5 A, AVK 2,5 A, AVK 2,5 A | O1010008_U4 | HD5573 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | MOTOR DE BEARING TEMPERATURE | ПОДШИПНИК ЭЛ ДВИГАТЕЛЯ 17-KM-101 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 100 |  | 0 | 150 | °C | [5 empty] | TS-Q-07:10/ O1010008_U4:1 | TS-Q-07:11/ O1010008_U4:3 | TS-Q-07:12/ O1010008_U4:4 |  | O1010008:4A/ O1010008_U4:5 | O1010008:4C/ O1010008_U4:6 | [6 empty] | 4A | 4C | 1 | 3 | 4 | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -11100 | 17TT11100 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Differential Pressure Transmitter | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-002FL11 | 12 Pair | Pr.08 | 17-MC-DCS-009 | TS-G-02 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U9 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-U-111 Deaerator storage tank | ТЕМПЕР В ДЕАЭРАТОРЕ 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 150 | °C | [5 empty] | TS-G-02:15/ O1010011_U9:3 | TS-G-02:16/ O1010011_U9:4 |  |  | O1010011:9A/ O1010011_U9:5 | O1010011:9C/ O1010011_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -11101 | 17TT11101 |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21711101 | DCS_AI_01 | Field |  | 17-C-AD-I-002FL11 | 12 Pair | Pr.09 | 17-MC-DCS-009 | TS-G-02 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U6 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | DM Water to 17-U-111 | ДЕМ ВОДА В 17-U-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 60 |  | -50 | 100 | °C | [5 empty] | TS-G-02:17/ O1010011_U6:3 | TS-G-02:18/ O1010011_U6:4 |  |  | O1010011:6A/ O1010011_U6:5 | O1010011:6C/ O1010011_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.12 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 08.04.25 сигнал 17TT11264 исключен по TQ-132 | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010009_U15 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 15 | AI713-H11 | 16 |  |  | демонтировать провода от клеммной группы TS-P-07 клеммы 1, 2 до барьера демонтировать клеммную группу TS-P-07 | DCS AMMONIA-UTILITIES | [25 empty] | O1010009:15A/ O1010009_U15:5 | O1010009:15C/ O1010009_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -11300 | 17TT11300 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21711301 | DCS_AI_02 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.16 | 17-MC-DCS-009 | TS-H-03 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010102R_U7 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From steam turbine of the Boiler supply fan | ПАР НД ОТ ТУРБИНЫ ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 200 | 270 |  | -50 | 360 | °C | [5 empty] | TS-H-03:31/ O1010102R_U7:3 | TS-H-03:32/ O1010102R_U7:4 |  |  | O1010102R:7A/ O1010102R_U7:5 | O1010102R:7C/ O1010102R_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -11300 | 17TY11300A |  | AO-R-IS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21711301 | DCS_AO_02 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.19 | 17-MC-DCS-009 | TS-H-03 | 37 | 38 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010110R_U14 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 14 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From steam turbine of the Boiler supply fan | ОТ ТУРБИНЫ ВЕНТИЛЯТОРА КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-H-03:37/ O1010110R_U14:3 | TS-H-03:38/ O1010110R_U14:4 |  |  | O1010110R:14A/ O1010110R_U14:5 | O1010110R:14C/ O1010110R_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -11302 | 17TT11302 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21711301 | DCS_AI_01 | Field |  | 17-C-AD-I-001FL11 | 24 Pair | Pr.17 | 17-MC-DCS-009 | TS-H-03 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011006_U13 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | From steam turbine of the Boiler supply fan | ПАР НД ОТ ТУРБИНЫ ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  | 278 |  | -50 | 360 | °C | [5 empty] | TS-H-03:33/ O1011006_U13:3 | TS-H-03:34/ O1011006_U13:4 |  |  | O1011006:13A/ O1011006_U13:5 | O1011006:13C/ O1011006_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -11303 | 17TT11303 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted (Temperature) | 4124-XZ-DM-21711301 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-AH001 | 12 Pair | Pr.09 | 17-MC-DCS-006 | TS-R-05 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U9 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CEMS for Star-Up-Boiler 17-L-111 | ДЫМОВЫЕ ГАЗЫ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | CEMS |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 120 | 160 |  | 0 | 162 | 0C | [5 empty] | TS-R-05:17/ O1010007_U9:3 | TS-R-05:18/ O1010007_U9:4 |  |  | O1010007:9A/ O1010007_U9:5 | O1010007:9C/ O1010007_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113501 | 17TT113501 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.10 | 17-MC-DCS-006 | TS-O-05 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010003_U16 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | FROM FW PUMPS 17-P-111A/B | НАГНЕТАНИЕ 17-P-111A/B | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 200 | °C | [5 empty] | TS-O-05:19/ O1010003_U16:3 | TS-O-05:20/ O1010003_U16:4 |  |  | O1010003:16A/ O1010003_U16:5 | O1010003:16C/ O1010003_U16:6 | [6 empty] | 16A | 16C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113504 | 17TT113504 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.11 | 17-MC-DCS-006 | TS-O-05 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010004_U1 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM DRUM LEVEL | НАГНЕТАНИЕ 17-P-111A/B ПОСЛЕ ЭКОНОМАЙЗЕРА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 300 | °C | [5 empty] | TS-O-05:21/ O1010004_U1:3 | TS-O-05:22/ O1010004_U1:4 |  |  | O1010004:1A/ O1010004_U1:5 | O1010004:1C/ O1010004_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113506 | 17TT113506 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.12 | 17-MC-DCS-006 | TS-O-05 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010004_U2 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | ACROSS STEAM HEADER 17-L-111-E-112 | ПАР НА ВЫХОДЕ С 1 СТ П/П ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 400 | °C | [5 empty] | TS-O-05:23/ O1010004_U2:3 | TS-O-05:24/ O1010004_U2:4 |  |  | O1010004:2A/ O1010004_U2:5 | O1010004:2C/ O1010004_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113509 | 17TT113509 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.13 | 17-MC-DCS-006 | TS-O-05 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010004_U3 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | ACROSS STEAM HEADER 17-L-111-E-112 | ОХЛ ПАР НА ВЫХОДЕ С 1 СТ П/П ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 400 | °C | [5 empty] | TS-O-05:25/ O1010004_U3:3 | TS-O-05:26/ O1010004_U3:4 |  |  | O1010004:3A/ O1010004_U3:5 | O1010004:3C/ O1010004_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -113509 | 17TY113509 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-FB-VD-BD00317L11111307_SH.1 | DCS_AO_02 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.13 | 17-MC-DCS-008 | TS-P-02 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010108R_U6 | HD5546 | O1010108R | TUA711-AIO16 | 17-SC-DCS-001/O1010108R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010108R | 9 | 6 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | STEAM DRUM LEVEL | УРОВЕНЬ В БАРАБАНЕ ПАРА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-02:25/ O1010108R_U6:3 | TS-P-02:26/ O1010108R_U6:4 |  |  | O1010108R:6A/ O1010108R_U6:5 | O1010108R:6C/ O1010108R_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113511 | 17TT113511 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111307_SH.2 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.14 | 17-MC-DCS-006 | TS-O-05 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010004_U4 | HD5542 | O1010004 | TUA711-AIO16 | 17-SC-DCS-001/O1010004/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010004 | 5 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO MP STEAM HEADER | ПАР ПОСЛЕ П/П ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 450 | °C | [5 empty] | TS-O-05:27/ O1010004_U4:3 | TS-O-05:28/ O1010004_U4:4 |  |  | O1010004:4A/ O1010004_U4:5 | O1010004:4C/ O1010004_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113520 | 17TT113520 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111303 | DCS_AI_02 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.01 | 17-MC-DCS-008 | TS-P-02 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010100R_U4 | HD5542 | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | AIR DUCT TEMPERATURE | ВОЗДУХ НА ГОРЕНИЕ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 50 | °C | [5 empty] | TS-P-02:1/ O1010100R_U4:3 | TS-P-02:2/ O1010100R_U4:4 |  |  | O1010100R:4A/ O1010100R_U4:5 | O1010100R:4C/ O1010100R_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113523 | 17TT113523 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.04 | 17-MC-DCS-008 | TS-P-02 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010010_U1 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CASING TEMPERATURE U/S ECO | ДЫМ ГАЗЫ ПУСКОВОГО КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 450 | °C | [5 empty] | TS-P-02:7/ O1010010_U1:3 | TS-P-02:8/ O1010010_U1:4 |  |  | O1010010:1A/ O1010010_U1:5 | O1010010:1C/ O1010010_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113525 | 17TT113525 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111303 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL11-L111 | 24 Pair | Pr.06 | 17-MC-DCS-008 | TS-P-02 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010010_U3 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | CASING TEMPERATURE D/S ECO | ДЫМ ГАЗЫ ПОСЛЕ ЭКОНОМАЙЗ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 450 | °C | [5 empty] | TS-P-02:11/ O1010010_U3:3 | TS-P-02:12/ O1010010_U3:4 |  |  | O1010010:3A/ O1010010_U3:5 | O1010010:3C/ O1010010_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113530 | 17TT113530 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Remote Mounted | 4124-FB-VD-BD00317L11111341 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L111 | 24 Pair | Pr.04 | 17-MC-DCS-006 | TS-O-05 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010006_U1 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | MP STEAM FROM DISTRIBUTION | ПАР СД НА ДУТЬЕВОЙ ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 450 | °C | [5 empty] | TS-O-05:7/ O1010006_U1:3 | TS-O-05:8/ O1010006_U1:4 |  |  | O1010006:1A/ O1010006_U1:5 | O1010006:1C/ O1010006_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113702 | 17TT113702 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111309 | DCS_AI_01 | Field |  | 17-C-AD-N-702FL11-L111 | 06 Pair | Pr.03 | 17-MC-DCS-006 | TS-Q-06 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010006_U13 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Oil Reservoir 17-L-111-T-111 | ТЭН МАСЛОБАКА ДУТ ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0.0 | 90 | °C | [5 empty] | TS-Q-06:5/ O1010006_U13:3 | TS-Q-06:6/ O1010006_U13:4 |  |  | O1010006:13A/ O1010006_U13:5 | O1010006:13C/ O1010006_U13:6 | [6 empty] | 13A | 13C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113704 | 17TT113704 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FB-VD-BD00317L11111309 | DCS_AI_01 | Field |  | 17-C-AD-N-702FL11-L111 | 06 Pair | Pr.01 | 17-MC-DCS-006 | TS-Q-06 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010006_U11 | HD5542 | O1010006 | TUA711-AIO16 | 17-SC-DCS-001/O1010006/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010006 | 7 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | To Oil Tank | СМ МАСЛО ПОСЛЕ М/Х ДУТ ВЕНТ ПУСК КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | 0 | 100 | °C | [5 empty] | TS-Q-06:1/ O1010006_U11:3 | TS-Q-06:2/ O1010006_U11:4 |  |  | O1010006:11A/ O1010006_U11:5 | O1010006:11C/ O1010006_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -113801 | 17TT113801 |  | AI-R-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Position Closed Proximity Switch | 4124-FB-VD-BD00317L11111372_SH.1 | DCS_AI_02 | Field |  | 17-C-AD-I-001FL11-L111 | 24 Pair | Pr.07 | 17-MC-DCS-009 | TS-H-04 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010102R_U11 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | TO ATMOSPHERE | ТОПЛИВНЫЙ ГАЗ НА КОТЕЛ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 80 | °C | [5 empty] | TS-H-04:13/ O1010102R_U11:3 | TS-H-04:14/ O1010102R_U11:4 |  |  | O1010102R:11A/ O1010102R_U11:5 | O1010102R:11C/ O1010102R_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -11801 | 17TT11801A |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21711801 | DCS_AI_01 | Field |  | 17-C-AD-I-003FL11 | 12 Pair | Pr.05 | 17-MC-DCS-009 | TS-G-03 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U11 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Fuel gas to Distribution | ТОПЛИВНЫЙ ГАЗ НА КОТЕЛ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 25 |  | -50 | 50 | °C | [5 empty] | TS-G-03:9/ O1010011_U11:3 | TS-G-03:10/ O1010011_U11:4 |  |  | O1010011:11A/ O1010011_U11:5 | O1010011:11C/ O1010011_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -11801 | 17TT11801B |  | AI-IS (4-20 mA, 2 wire) DCS |  | Сигнал | Pressure Transmitter | 4124-XZ-DM-21711801 | DCS_AI_01 | Field |  | 17-C-AD-I-003FL11 | 12 Pair | Pr.06 | 17-MC-DCS-009 | TS-G-03 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010011_U14 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Fuel gas to Distribution | ТОПЛИВНЫЙ ГАЗ НА КОТЕЛ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 25 |  | -50 | 50 | °C | [5 empty] | TS-G-03:11/ O1010011_U14:3 | TS-G-03:12/ O1010011_U14:4 |  |  | O1010011:14A/ O1010011_U14:5 | O1010011:14C/ O1010011_U14:6 | [6 empty] | 14A | 14C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -11801 | 17TY11801 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21711801 | DCS_AO_02 | Thristor Contol panel |  | 17-B-AD-N-002BL02 | 06 Pair | Pr.01 | 17-MC-DCS-006 | TS-O-06 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010104R_U9 | HD5546 | O1010104R | TUA711-AIO16 | 17-SC-DCS-001/O1010104R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010104R | 5 | 9 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-111 Fuel Gas Electrical heater | ТОПЛ ГАЗ ЭЛЕКТОНАГРЕВАТЕЛЬ E111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-06:1/ O1010104R_U9:3 | TS-O-06:2/ O1010104R_U9:4 |  |  | O1010104R:9A/ O1010104R_U9:5 | O1010104R:9C/ O1010104R_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -11884 | 17TI11884 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Indicator | 4124-XZ-DM-21711801 | DCS_AI_01 | Thristor Contol panel |  | 17-B-AD-N-002BL02 | 06 Pair | Pr.02 | 17-MC-DCS-006 | TS-O-06 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010000_U1 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-111 Fuel Gas Electrical heater | КОЖУХ 17-E-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 600 | 0C | [5 empty] | TS-O-06:3/ O1010000_U1:3 | TS-O-06:4/ O1010000_U1:4 |  |  | O1010000:1A/ O1010000_U1:5 | O1010000:1C/ O1010000_U1:6 | [6 empty] | 1A | 1C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -11885 | 17TI11885 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Indicator | 4124-XZ-DM-21711801 | DCS_AI_01 | Thristor Contol panel |  | 17-B-AD-N-002BL02 | 06 Pair | Pr.03 | 17-MC-DCS-006 | TS-O-06 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010000_U2 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-001 Fuel Gas Electrical heater | КОЖУХ 17-E-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 600 | 0C | [5 empty] | TS-O-06:5/ O1010000_U2:3 | TS-O-06:6/ O1010000_U2:4 |  |  | O1010000:2A/ O1010000_U2:5 | O1010000:2C/ O1010000_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -11886 | 17TI11886 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Indicator | 4124-XZ-DM-21711801 | DCS_AI_01 | Thristor Contol panel |  | 17-B-AD-N-002BL02 | 06 Pair | Pr.04 | 17-MC-DCS-006 | TS-O-06 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010000_U3 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-001 Fuel Gas Electrical heater | КОЖУХ 17-E-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 600 | 0C | [5 empty] | TS-O-06:7/ O1010000_U3:3 | TS-O-06:8/ O1010000_U3:4 |  |  | O1010000:3A/ O1010000_U3:5 | O1010000:3C/ O1010000_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -11887 | 17TI11887 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Indicator | 4124-XZ-DM-21711801 | DCS_AI_01 | Thristor Contol panel |  | 17-B-AD-N-002BL02 | 06 Pair | Pr.05 | 17-MC-DCS-006 | TS-O-06 | 9 | 10 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010000_U4 | HD5542 | O1010000 | TUA711-AIO16 | 17-SC-DCS-001/O1010000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010000 | 1 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-E-111 Fuel Gas Electrical heater | ТЭН 17-E-111 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -50 | 600 | 0C | [5 empty] | TS-O-06:9/ O1010000_U4:3 | TS-O-06:10/ O1010000_U4:4 |  |  | O1010000:4A/ O1010000_U4:5 | O1010000:4C/ O1010000_U4:6 | [6 empty] | 4A | 4C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -13001 | 17TT13001 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21713001 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.17 | 17-MC-DCS-006 | TS-O-02 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010014R_U15 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-131 Temp | БАК ВОДЫ 17-V-131 | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 20 | 35 |  | -50 | 50 | °C | [5 empty] | TS-O-02:33/ O1010014R_U15:3 | TS-O-02:34/ O1010014R_U15:4 |  |  | O1010014R:15A/ O1010014R_U15:5 | O1010014R:15C/ O1010014R_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -13001 | 17TY13001 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21713001 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL10 | 24 Pair | Pr.03 | 17-MC-DCS-006 | TS-O-02 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011012R_U3 | HD5546 | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 3 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-131 Temp | ТЕМПЕРАТУРА В БАКЕ ВОДЫ 17-V-131 | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-02:5/ O1011012R_U3:3 | TS-O-02:6/ O1011012R_U3:4 |  |  | O1011012R:3A/ O1011012R_U3:5 | O1011012R:3C/ O1011012R_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -14001 | 17TT14001 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21714001 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL14 | 12 Pair | Pr.04 | 17-MC-DCS-008 | TS-O-05 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011001_U15 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-BS-143A/B First Flush Basins | 17-BS-143A/B СБОРНИК СТОКОВ | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 50 |  | -50 | 80 | °C | [5 empty] | TS-O-05:7/ O1011001_U15:3 | TS-O-05:8/ O1011001_U15:4 |  |  | O1011001:15A/ O1011001_U15:5 | O1011001:15C/ O1011001_U15:6 | [6 empty] | 15A | 15C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -14003 | 17TT14003 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21714002 | DCS_AI_01 | Field |  | 17-C-AD-N-002FL14 | 12 Pair | Pr.05 | 17-MC-DCS-008 | TS-O-05 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011002_U11 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-BS-144 Rain Water Retention Basin | 17-BS-144 СБОРНИК ЛИВНЕВЫХ ВОД | 17-AMMONIA UTILITIES | 14-Wastewater Treatment Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 5 | 50 |  | -50 | 80 | °C | [5 empty] | TS-O-05:9/ O1011002_U11:3 | TS-O-05:10/ O1011002_U11:4 |  |  | O1011002:11A/ O1011002_U11:5 | O1011002:11C/ O1011002_U11:6 | [6 empty] | 11A | 11C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -17101 | 17TT17101 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21717101 | DCS_AI_02 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.11 | 17-MC-DCS-008 | TS-O-02 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011010R_U6 | HD5542 | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Hot Glycol Water supply to Distribution | ПОДОГРЕТЫЙ ГЛИКОЛИВЫЙ РАСТВОР | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | 17-TI-17101 | 17-TI-17102 | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 70 | 105 |  | -50 | 150 | °C | [5 empty] | TS-O-02:21/ O1011010R_U6:3 | TS-O-02:22/ O1011010R_U6:4 |  |  | O1011010R:6A/ O1011010R_U6:5 | O1011010R:6C/ O1011010R_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-T -17101 | 17TY17101 |  | AO-R-NIS (4-20 mA) DCS |  | Сигнал | Smart Positioner | 4124-XZ-DM-21717101 | DCS_AO_02 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.15 | 17-MC-DCS-008 | TS-O-02 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011014R_U6 | HD5546 | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 6 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Hot Glycol Water supply to Distribution | ПОДАЧА ГОР ВОДНО-ГЛИКОЛ В 17E171 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-02:29/ O1011014R_U6:3 | TS-O-02:30/ O1011014R_U6:4 |  |  | O1011014R:6A/ O1011014R_U6:5 | O1011014R:6C/ O1011014R_U6:6 | [6 empty] | 6A | 6C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -17102 | 17TT17102 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21717101 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.12 | 17-MC-DCS-008 | TS-O-02 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011001_U7 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Hot Glycol Water supply to Distribution | ПОДОГРЕТЫЙ ГЛИКОЛИВЫЙ РАСТВОР | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 70 | 105 |  | -50 | 150 | °C | [5 empty] | TS-O-02:23/ O1011001_U7:3 | TS-O-02:24/ O1011001_U7:4 |  |  | O1011001:7A/ O1011001_U7:5 | O1011001:7C/ O1011001_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -17103 | 17TT17103 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21717101 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.13 | 17-MC-DCS-008 | TS-O-02 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011001_U8 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | Pump 17-P-171A Suction line | ОБРАТНЫЙ КОЛЛЕКТОР ГЛИКОЛ РАСТВОРА | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 10 | 80 |  | -50 | 100 | °C | [5 empty] | TS-O-02:25/ O1011001_U8:3 | TS-O-02:26/ O1011001_U8:4 |  |  | O1011001:8A/ O1011001_U8:5 | O1011001:8C/ O1011001_U8:6 | [6 empty] | 8A | 8C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T -17104 | 17TT17104 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-XZ-DM-21717101 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL17 | 24 Pair | Pr.14 | 17-MC-DCS-008 | TS-O-02 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011001_U9 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | 17-V-171 Glycol water expansion vessel | РАСШ БАК ГЛИКОЛИВОГО РАСТВОРА 17-V-171 | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | 10 | 80 |  | -50 | 100 | °C | [5 empty] | TS-O-02:27/ O1011001_U9:3 | TS-O-02:28/ O1011001_U9:4 |  |  | O1011001:9A/ O1011001_U9:5 | O1011001:9C/ O1011001_U9:6 | [6 empty] | 9A | 9C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T-1001 | 17TT1001 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Smart Positioner |  | DCS_AI_01 | Field |  | 17-С-AD-I-1-FL90 | 15 Pair | Pr.01 | 17-MC-DCS-009 | TS-H-05 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A | O1011005_U7 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | The temperature of HHP nitrogen in the pipeline from Ammonia-2 to Ammonia-1 | АЗОТ СВД ОТ АММИАКА-2 НА АММИАК-1 | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -40 | 100 | °C | [5 empty] | TS-H-05:1/ O1011005_U7:3 | TS-H-05:2/ O1011005_U7:4 |  |  | O1011005:7A/ O1011005_U7:5 | O1011005:7C/ O1011005_U7:6 | [6 empty] | 7A | 7C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T-1002 | 17TT1002 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Smart Positioner |  | DCS_AI_01 | Field |  | 17-С-AD-I-1-FL90 | 15 Pair | Pr.02 | 17-MC-DCS-009 | TS-H-05 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A | O1011005_U2 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | The temperature of HHP nitrogen in the pipeline from Ammonia-2 to Ammonia-1 | АЗОТ СВД ОТ АММИАКА-2 НА КАРБАМИД | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -40 | 100 | °C | [5 empty] | TS-H-05:3/ O1011005_U2:3 | TS-H-05:4/ O1011005_U2:4 |  |  | O1011005:2A/ O1011005_U2:5 | O1011005:2C/ O1011005_U2:6 | [6 empty] | 2A | 2C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T-1003 | 17TT1003 |  | AI-IS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Smart Positioner |  | DCS_AI_01 | Field |  | 17-С-AD-I-1-FL90 | 15 Pair | Pr.03 | 17-MC-DCS-009 | TS-H-05 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A | O1011005_U3 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | LPCarbon Dioxide Temperature in the Ammonia-1 and 2 Pipeline to Urea | СО2 НД ОТ АММИАКА-2 НА КАРБАМИД | 17-AMMONIA UTILITIES | 00-Inter-factory | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -40 | 100 | °C | [5 empty] | TS-H-05:5/ O1011005_U3:3 | TS-H-05:6/ O1011005_U3:4 |  |  | O1011005:3A/ O1011005_U3:5 | O1011005:3C/ O1011005_U3:6 | [6 empty] | 3A | 3C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.11 | 17-T-115300 | 17TT115300 |  | AI-NIS (4-20 mA, 2 wire) DCS | 07.04.25 изм TAG_SERVICE_RU по TQ-131 | Сигнал | Temperature Transmitter - Head Mounted | 4124-FY-VD-BD17117L11400001 | DCS_AI_01 | Field |  | 17-C-AD-N-001FL11-L112 | 12 Pair | Pr.04 | 17-MC-DCS-006 | TS-R-01 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010007_U10 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | HEATING UNIT 17-L-114 | ТЕМПЕРАТУРА В ДОЗАТОРНОЙ КОТЛА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  |  |  |  | -40 | 50 | °C | [5 empty] | TS-R-01:7/ O1010007_U10:3 | TS-R-01:8/ O1010007_U10:4 |  |  | O1010007:10A/ O1010007_U10:5 | O1010007:10C/ O1010007_U10:6 | [6 empty] | 10A | 10C | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -01003 | 17XS01003X |  | DI-NIS (VFC) DCS |  | Сигнал | Exchange Signal | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-007BL02 | 01 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-09 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Interlock 17-I-1003 | БЛОКИРОВКА 17-I-1003 СИГНАЛИЗ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | ESD | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-09:1/ O1011113:11A | TS-F-09:2/ O1011113:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020201 -A | 17XZSH020201A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.01 | 17-MC-DCS-002 | TS-O-07 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U1 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Outlet / Vent | 11-XV-020201-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:1/ O1011101_U1:3 | TS-O-07:2/ O1011101_U1:4 |  |  | O1011101:1A/ O1011101_U1:5 | O1011101:1B/ O1011101_U1:6 | [6 empty] | 1A | 1B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020201 -A | 17XZSL020201A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.02 | 17-MC-DCS-002 | TS-O-07 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U2 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Outlet / Vent | 11-XV-020201-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:3/ O1011101_U2:3 | TS-O-07:4/ O1011101_U2:4 |  |  | O1011101:2A/ O1011101_U2:5 | O1011101:2B/ O1011101_U2:6 | [6 empty] | 2A | 2B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020201 -A | 17XY020201A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL03-L022 | 30 Core | C.01 | 17-MC-DCS-002 | TS-O-01 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 1 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Outlet / Vent | ПРОМЫВКА КАТИОНООБМЕННИУА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-01:1/ O1011202:1A | TS-O-01:2/ O1011202:1C | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020201 -B | 17XZSH020201B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.01 | 17-MC-DCS-002 | TS-R-01 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U11 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Outlet / Vent | 11-XV-020201-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:1/ O1011101_U11:3 | TS-R-01:2/ O1011101_U11:4 |  |  | O1011101:11A/ O1011101_U11:5 | O1011101:11B/ O1011101_U11:6 | [6 empty] | 11A | 11B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020201 -B | 17XZSL020201B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.02 | 17-MC-DCS-002 | TS-R-01 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U12 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Outlet / Vent | 11-XV-020201-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:3/ O1011101_U12:3 | TS-R-01:4/ O1011101_U12:4 |  |  | O1011101:12A/ O1011101_U12:5 | O1011101:12B/ O1011101_U12:6 | [6 empty] | 12A | 12B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020201 -B | 17XY020201B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL03-L022 | 16 Core | C.01 | 17-MC-DCS-002 | TS-O-03 | 1 | 2 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 17 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Outlet / Vent | SAC КАТИОНООБМЕН С ОБР ПРОМЫВКОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-03:1/ O1011202:17A | TS-O-03:2/ O1011202:17C | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020201 -C | 17XZSH020201C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.01 | 17-MC-DCS-002 | TS-R-02 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U21 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Outlet / Vent | 11-XV-020202-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:1/ O1011101_U21:3 | TS-R-02:2/ O1011101_U21:4 |  |  | O1011101:21A/ O1011101_U21:5 | O1011101:21B/ O1011101_U21:6 | [6 empty] | 21A | 21B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020201 -C | 17XZSL020201C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.02 | 17-MC-DCS-002 | TS-R-02 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U22 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Outlet / Vent | 11-XV-020202-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:3/ O1011101_U22:3 | TS-R-02:4/ O1011101_U22:4 |  |  | O1011101:22A/ O1011101_U22:5 | O1011101:22B/ O1011101_U22:6 | [6 empty] | 22A | 22B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020201 -C | 17XY020201C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL03-L022 | 16 Core | C.01 | 17-MC-DCS-002 | TS-O-04 | 1 | 2 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 23 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Outlet / Vent | SAC КАТИОНООБМЕН С ОБР ПРОМЫВКОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-04:1/ O1011202:23A | TS-O-04:2/ O1011202:23C | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020202 -A | 17XZSH020202A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.03 | 17-MC-DCS-002 | TS-O-07 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U3 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger diluted acid inlet | 11-XV-020202-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:5/ O1011101_U3:3 | TS-O-07:6/ O1011101_U3:4 |  |  | O1011101:3A/ O1011101_U3:5 | O1011101:3B/ O1011101_U3:6 | [6 empty] | 3A | 3B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020202 -A | 17XZSL020202A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.04 | 17-MC-DCS-002 | TS-O-07 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U4 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger diluted acid inlet | 11-XV-020202-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:7/ O1011101_U4:3 | TS-O-07:8/ O1011101_U4:4 |  |  | O1011101:4A/ O1011101_U4:5 | O1011101:4B/ O1011101_U4:6 | [6 empty] | 4A | 4B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020202 -A | 17XY020202A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL03-L022 | 30 Core | C.03 | 17-MC-DCS-002 | TS-O-01 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 2 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger diluted acid inlet | SAC КАТИОНООБМЕН РАЗБАВ КИСЛОТА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-01:3/ O1011202:2A | TS-O-01:4/ O1011202:2C | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020202 -B | 17XZSH020202B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.03 | 17-MC-DCS-002 | TS-R-01 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U13 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger diluted acid inlet | 11-XV-020202-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:5/ O1011101_U13:3 | TS-R-01:6/ O1011101_U13:4 |  |  | O1011101:13A/ O1011101_U13:5 | O1011101:13B/ O1011101_U13:6 | [6 empty] | 13A | 13B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020202 -B | 17XZSL020202B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.04 | 17-MC-DCS-002 | TS-R-01 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U14 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger diluted acid inlet | 11-XV-020202-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:7/ O1011101_U14:3 | TS-R-01:8/ O1011101_U14:4 |  |  | O1011101:14A/ O1011101_U14:5 | O1011101:14B/ O1011101_U14:6 | [6 empty] | 14A | 14B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020202 -B | 17XY020202B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL03-L022 | 16 Core | C.03 | 17-MC-DCS-002 | TS-O-03 | 3 | 4 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 18 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger diluted acid inlet | SAC КАТИОНООБМЕН РАЗБАВ КИСЛОТА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-03:3/ O1011202:18A | TS-O-03:4/ O1011202:18C | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020202 -C | 17XZSH020202C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.03 | 17-MC-DCS-002 | TS-R-02 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U23 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger diluted acid inlet | 11-XV-020202-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:5/ O1011101_U23:3 | TS-R-02:6/ O1011101_U23:4 |  |  | O1011101:23A/ O1011101_U23:5 | O1011101:23B/ O1011101_U23:6 | [6 empty] | 23A | 23B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020202 -C | 17XZSL020202C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.04 | 17-MC-DCS-002 | TS-R-02 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U24 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger diluted acid inlet | 11-XV-020202-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:7/ O1011101_U24:3 | TS-R-02:8/ O1011101_U24:4 |  |  | O1011101:24A/ O1011101_U24:5 | O1011101:24B/ O1011101_U24:6 | [6 empty] | 24A | 24B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020202 -C | 17XY020202C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL03-L022 | 16 Core | C.03 | 17-MC-DCS-002 | TS-O-04 | 3 | 4 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 24 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger diluted acid inlet | SAC КАТИОНООБМЕН РАЗБАВ КИСЛОТА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-04:3/ O1011202:24A | TS-O-04:4/ O1011202:24C | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020203 -A | 17XZSH020203A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.05 | 17-MC-DCS-002 | TS-O-07 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U5 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Inlet | 11-XV-020203-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:9/ O1011101_U5:3 | TS-O-07:10/ O1011101_U5:4 |  |  | O1011101:5A/ O1011101_U5:5 | O1011101:5B/ O1011101_U5:6 | [6 empty] | 5A | 5B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020203 -A | 17XZSL020203A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.06 | 17-MC-DCS-002 | TS-O-07 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U6 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Inlet | 11-XV-020203-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:11/ O1011101_U6:3 | TS-O-07:12/ O1011101_U6:4 |  |  | O1011101:6A/ O1011101_U6:5 | O1011101:6B/ O1011101_U6:6 | [6 empty] | 6A | 6B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020203 -A | 17XY020203A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL03-L022 | 30 Core | C.05 | 17-MC-DCS-002 | TS-O-01 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 3 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Inlet | SAC КАТИОНООБМЕН С ОБР ПРОМЫВКОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-01:5/ O1011202:3A | TS-O-01:6/ O1011202:3C | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020203 -B | 17XZSH020203B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.05 | 17-MC-DCS-002 | TS-R-01 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U15 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Inlet | 11-XV-020203-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:9/ O1011101_U15:3 | TS-R-01:10/ O1011101_U15:4 |  |  | O1011101:15A/ O1011101_U15:5 | O1011101:15B/ O1011101_U15:6 | [6 empty] | 15A | 15B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020203 -B | 17XZSL020203B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.06 | 17-MC-DCS-002 | TS-R-01 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U16 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Inlet | 11-XV-020203-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:11/ O1011101_U16:3 | TS-R-01:12/ O1011101_U16:4 |  |  | O1011101:16A/ O1011101_U16:5 | O1011101:16B/ O1011101_U16:6 | [6 empty] | 16A | 16B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020203 -B | 17XY020203B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL03-L022 | 16 Core | C.05 | 17-MC-DCS-002 | TS-O-03 | 5 | 6 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 19 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Inlet | SAC КАТИОНООБМЕН С ОБР ПРОМЫВКОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-03:5/ O1011202:19A | TS-O-03:6/ O1011202:19C | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020203 -C | 17XZSH020203C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.05 | 17-MC-DCS-002 | TS-R-02 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U25 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Inlet | 11-XV-020203-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:9/ O1011101_U25:3 | TS-R-02:10/ O1011101_U25:4 |  |  | O1011101:25A/ O1011101_U25:5 | O1011101:25B/ O1011101_U25:6 | [6 empty] | 25A | 25B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020203 -C | 17XZSL020203C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.06 | 17-MC-DCS-002 | TS-R-02 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U26 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Inlet | 11-XV-020203-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:11/ O1011101_U26:3 | TS-R-02:12/ O1011101_U26:4 |  |  | O1011101:26A/ O1011101_U26:5 | O1011101:26B/ O1011101_U26:6 | [6 empty] | 26A | 26B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020203 -C | 17XY020203C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL03-L022 | 16 Core | C.05 | 17-MC-DCS-002 | TS-O-04 | 5 | 6 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 25 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Backwash Inlet | SAC КАТИОНООБМЕН С ОБР ПРОМЫВКОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-04:5/ O1011202:25A | TS-O-04:6/ O1011202:25C | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020204 -A | 17XZSH020204A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.07 | 17-MC-DCS-002 | TS-O-07 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U7 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Outlet | 11-XV-020204-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:13/ O1011101_U7:3 | TS-O-07:14/ O1011101_U7:4 |  |  | O1011101:7A/ O1011101_U7:5 | O1011101:7B/ O1011101_U7:6 | [6 empty] | 7A | 7B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020204 -A | 17XZSL020204A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.08 | 17-MC-DCS-002 | TS-O-07 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U8 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Outlet | 11-XV-020204-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:15/ O1011101_U8:3 | TS-O-07:16/ O1011101_U8:4 |  |  | O1011101:8A/ O1011101_U8:5 | O1011101:8B/ O1011101_U8:6 | [6 empty] | 8A | 8B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020204 -A | 17XY020204A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL03-L022 | 30 Core | C.07 | 17-MC-DCS-002 | TS-O-01 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 4 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Outlet | ВЫХОД КАТИОНООБМЕННИКА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-01:7/ O1011202:4A | TS-O-01:8/ O1011202:4C | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020204 -B | 17XZSH020204B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.07 | 17-MC-DCS-002 | TS-R-01 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U17 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Outlet | 11-XV-020204-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:13/ O1011101_U17:3 | TS-R-01:14/ O1011101_U17:4 |  |  | O1011101:17A/ O1011101_U17:5 | O1011101:17B/ O1011101_U17:6 | [6 empty] | 17A | 17B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020204 -B | 17XZSL020204B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.08 | 17-MC-DCS-002 | TS-R-01 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U18 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Outlet | 11-XV-020204-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:15/ O1011101_U18:3 | TS-R-01:16/ O1011101_U18:4 |  |  | O1011101:18A/ O1011101_U18:5 | O1011101:18B/ O1011101_U18:6 | [6 empty] | 18A | 18B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020204 -B | 17XY020204B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL03-L022 | 16 Core | C.07 | 17-MC-DCS-002 | TS-O-03 | 7 | 8 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 20 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Outlet | ВЫХОД КАТИОНООБМЕННИКА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-03:7/ O1011202:20A | TS-O-03:8/ O1011202:20C | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020204 -C | 17XZSH020204C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.07 | 17-MC-DCS-002 | TS-R-02 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U27 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Outlet | 11-XV-020204-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:13/ O1011101_U27:3 | TS-R-02:14/ O1011101_U27:4 |  |  | O1011101:27A/ O1011101_U27:5 | O1011101:27B/ O1011101_U27:6 | [6 empty] | 27A | 27B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020204 -C | 17XZSL020204C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.08 | 17-MC-DCS-002 | TS-R-02 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U28 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Outlet | 11-XV-020204-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:15/ O1011101_U28:3 | TS-R-02:16/ O1011101_U28:4 |  |  | O1011101:28A/ O1011101_U28:5 | O1011101:28B/ O1011101_U28:6 | [6 empty] | 28A | 28B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020204 -C | 17XY020204C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL03-L022 | 16 Core | C.07 | 17-MC-DCS-002 | TS-O-04 | 7 | 8 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 26 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Outlet | ВЫХОД КАТИОНООБМЕННИКА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-04:7/ O1011202:26A | TS-O-04:8/ O1011202:26C | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020205 -A | 17XZSH020205A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.09 | 17-MC-DCS-002 | TS-O-07 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U9 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Drain | 11-XV-020205-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:17/ O1011101_U9:3 | TS-O-07:18/ O1011101_U9:4 |  |  | O1011101:9A/ O1011101_U9:5 | O1011101:9B/ O1011101_U9:6 | [6 empty] | 9A | 9B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020205 -A | 17XZSL020205A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL03-L022 | 12 Pair | Pr.10 | 17-MC-DCS-002 | TS-O-07 | 19 | 20 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U10 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Drain | 11-XV-020205-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-O-07:19/ O1011101_U10:3 | TS-O-07:20/ O1011101_U10:4 |  |  | O1011101:10A/ O1011101_U10:5 | O1011101:10B/ O1011101_U10:6 | [6 empty] | 10A | 10B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020205 -A | 17XY020205A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL03-L022 | 30 Core | C.09 | 17-MC-DCS-002 | TS-O-01 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 5 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Drain | ДРЕНАЖ КАТИОНООБМЕННИКА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-01:9/ O1011202:5A | TS-O-01:10/ O1011202:5C | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020205 -B | 17XZSH020205B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.09 | 17-MC-DCS-002 | TS-R-01 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U19 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Drain | 11-XV-020205-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:17/ O1011101_U19:3 | TS-R-01:18/ O1011101_U19:4 |  |  | O1011101:19A/ O1011101_U19:5 | O1011101:19B/ O1011101_U19:6 | [6 empty] | 19A | 19B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020205 -B | 17XZSL020205B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL03-L022 | 12 Pair | Pr.10 | 17-MC-DCS-002 | TS-R-01 | 19 | 20 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U20 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Drain | 11-XV-020205-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-01:19/ O1011101_U20:3 | TS-R-01:20/ O1011101_U20:4 |  |  | O1011101:20A/ O1011101_U20:5 | O1011101:20B/ O1011101_U20:6 | [6 empty] | 20A | 20B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020205 -B | 17XY020205B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL03-L022 | 16 Core | C.09 | 17-MC-DCS-002 | TS-O-03 | 9 | 10 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 21 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Drain | ДРЕНАЖ КАТИОНООБМЕННИКА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-03:9/ O1011202:21A | TS-O-03:10/ O1011202:21C | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020205 -C | 17XZSH020205C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.09 | 17-MC-DCS-002 | TS-R-02 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U29 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Drain | 11-XV-020205-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:17/ O1011101_U29:3 | TS-R-02:18/ O1011101_U29:4 |  |  | O1011101:29A/ O1011101_U29:5 | O1011101:29B/ O1011101_U29:6 | [6 empty] | 29A | 29B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020205 -C | 17XZSL020205C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL03-L022 | 12 Pair | Pr.10 | 17-MC-DCS-002 | TS-R-02 | 19 | 20 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011101_U30 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Drain | 11-XV-020205-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-02:19/ O1011101_U30:3 | TS-R-02:20/ O1011101_U30:4 |  |  | O1011101:30A/ O1011101_U30:5 | O1011101:30B/ O1011101_U30:6 | [6 empty] | 30A | 30B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020205 -C | 17XY020205C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.1 | DCS_DO_01 | Field |  | 17-C-CD-N-003FL03-L022 | 16 Core | C.09 | 17-MC-DCS-002 | TS-O-04 | 9 | 10 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 27 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | SAC Cationic Exchanger Drain | ДРЕНАЖ КАТИОНООБМЕННИКА SAC | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-04:9/ O1011202:27A | TS-O-04:10/ O1011202:27C | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020206 | 17XZSH020206 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.17 | 17-MC-DCS-002 | TS-R-04 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U15 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Water from rinse pumps to mixed beds | 17-XV-020206 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:33/ O1011102_U15:3 | TS-R-04:34/ O1011102_U15:4 |  |  | O1011102:15A/ O1011102_U15:5 | O1011102:15B/ O1011102_U15:6 | [6 empty] | 15A | 15B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020206 | 17XZSL020206 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.18 | 17-MC-DCS-002 | TS-R-04 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U16 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Water from rinse pumps to mixed beds | 17-XV-020206 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:35/ O1011102_U16:3 | TS-R-04:36/ O1011102_U16:4 |  |  | O1011102:16A/ O1011102_U16:5 | O1011102:16B/ O1011102_U16:6 | [6 empty] | 16A | 16B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020206 | 17XY020206 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.01 | 17-MC-DCS-002 | TS-O-05 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 29 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Water from rinse pumps to mixed beds | ВОДА ПРОМЫВКИ В СМЕШАННЫЙ СЛОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:1/ O1011202:29A | TS-O-05:2/ O1011202:29C | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020207 -A | 17XZSH020207A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.01 | 17-MC-DCS-002 | TS-R-04 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011101_U31 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Backwash Outlet / Vent | 17-XV-020207-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:1/ O1011101_U31:3 | TS-R-04:2/ O1011101_U31:4 |  |  | O1011101:31A/ O1011101_U31:5 | O1011101:31B/ O1011101_U31:6 | [6 empty] | 31A | 31B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020207 -A | 17XZSL020207A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.02 | 17-MC-DCS-002 | TS-R-04 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011101_U32 | HD5516 | O1011101 | TUA711-DIO32 | 17-SC-DCS-002/O1011101/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011101 | 2 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Backwash Outlet / Vent | 17-XV-020207-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:3/ O1011101_U32:3 | TS-R-04:4/ O1011101_U32:4 |  |  | O1011101:32A/ O1011101_U32:5 | O1011101:32B/ O1011101_U32:6 | [6 empty] | 32A | 32B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020207 -A | 17XY020207A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.03 | 17-MC-DCS-002 | TS-O-05 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 30 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Backwash Outlet / Vent | ВЫХОД ПРОМЫВКИ/ВЕНТ СМЕШ СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:3/ O1011202:30A | TS-O-05:4/ O1011202:30C | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020207 -B | 17XZSH020207B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.01 | 17-MC-DCS-002 | TS-P-05 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U17 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Backwash Outlet / Vent | 17-XV-020207-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:1/ O1011102_U17:3 | TS-P-05:2/ O1011102_U17:4 |  |  | O1011102:17A/ O1011102_U17:5 | O1011102:17B/ O1011102_U17:6 | [6 empty] | 17A | 17B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020207 -B | 17XZSL020207B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.02 | 17-MC-DCS-002 | TS-P-05 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U18 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Backwash Outlet / Vent | 17-XV-020207-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:3/ O1011102_U18:3 | TS-P-05:4/ O1011102_U18:4 |  |  | O1011102:18A/ O1011102_U18:5 | O1011102:18B/ O1011102_U18:6 | [6 empty] | 18A | 18B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020207 -B | 17XY020207B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.01 | 17-MC-DCS-002 | TS-O-06 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 7 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Backwash Outlet / Vent | ВЫХОД ПРОМЫВКИ/ВЕНТ СМЕШ СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:1/ O1011203:7A | TS-O-06:2/ O1011203:7C | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020207 -C | 17XZSH020207C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-01 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U1 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Backwash Outlet / Vent | 17-XV-020207-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:1/ O1011103_U1:3 | TS-Q-01:2/ O1011103_U1:4 |  |  | O1011103:1A/ O1011103_U1:5 | O1011103:1B/ O1011103_U1:6 | [6 empty] | 1A | 1B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020207 -C | 17XZSL020207C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.02 | 17-MC-DCS-002 | TS-Q-01 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U2 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Backwash Outlet / Vent | 17-XV-020207-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:3/ O1011103_U2:3 | TS-Q-01:4/ O1011103_U2:4 |  |  | O1011103:2A/ O1011103_U2:5 | O1011103:2B/ O1011103_U2:6 | [6 empty] | 2A | 2B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020207 -C | 17XY020207C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.01 | 17-MC-DCS-002 | TS-P-01 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 18 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Backwash Outlet / Vent | ВЫХОД ПРОМЫВКИ/ВЕНТ СМЕШ СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:1/ O1011203:18A | TS-P-01:2/ O1011203:18C | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020210 -A | 17XZSH020210A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.03 | 17-MC-DCS-002 | TS-R-04 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U1 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Eluates | 17-XV-020210-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:5/ O1011102_U1:3 | TS-R-04:6/ O1011102_U1:4 |  |  | O1011102:1A/ O1011102_U1:5 | O1011102:1B/ O1011102_U1:6 | [6 empty] | 1A | 1B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020210 -A | 17XZSL020210A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.04 | 17-MC-DCS-002 | TS-R-04 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U2 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Eluates | 17-XV-020210-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:7/ O1011102_U2:3 | TS-R-04:8/ O1011102_U2:4 |  |  | O1011102:2A/ O1011102_U2:5 | O1011102:2B/ O1011102_U2:6 | [6 empty] | 2A | 2B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020210 -A | 17XY020210A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.05 | 17-MC-DCS-002 | TS-O-05 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 31 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Eluates | СМЕШАННЫЙ СЛОЙ ??? | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:5/ O1011202:31A | TS-O-05:6/ O1011202:31C | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020210 -B | 17XZSH020210B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.03 | 17-MC-DCS-002 | TS-P-05 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U19 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Eluates | XV-020210-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:5/ O1011102_U19:3 | TS-P-05:6/ O1011102_U19:4 |  |  | O1011102:19A/ O1011102_U19:5 | O1011102:19B/ O1011102_U19:6 | [6 empty] | 19A | 19B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020210 -B | 17XZSL020210B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.04 | 17-MC-DCS-002 | TS-P-05 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U20 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Eluates | XV-020210-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:7/ O1011102_U20:3 | TS-P-05:8/ O1011102_U20:4 |  |  | O1011102:20A/ O1011102_U20:5 | O1011102:20B/ O1011102_U20:6 | [6 empty] | 20A | 20B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020210 -B | 17XY020210B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.03 | 17-MC-DCS-002 | TS-O-06 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 8 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Eluates | СМЕШАННЫЙ СЛОЙ ??? | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:3/ O1011203:8A | TS-O-06:4/ O1011203:8C | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020210 -C | 17XZSH020210C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.03 | 17-MC-DCS-002 | TS-Q-01 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U3 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Eluates | 17-XV-020210-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:5/ O1011103_U3:3 | TS-Q-01:6/ O1011103_U3:4 |  |  | O1011103:3A/ O1011103_U3:5 | O1011103:3B/ O1011103_U3:6 | [6 empty] | 3A | 3B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020210 -C | 17XZSL020210C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.04 | 17-MC-DCS-002 | TS-Q-01 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U4 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Eluates | 17-XV-020210-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:7/ O1011103_U4:3 | TS-Q-01:8/ O1011103_U4:4 |  |  | O1011103:4A/ O1011103_U4:5 | O1011103:4B/ O1011103_U4:6 | [6 empty] | 4A | 4B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020210 -C | 17XY020210C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.03 | 17-MC-DCS-002 | TS-P-01 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 19 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Eluates | СМЕШАННЫЙ СЛОЙ ??? | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:3/ O1011203:19A | TS-P-01:4/ O1011203:19C | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020211 -A | 17XZSH020211A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.05 | 17-MC-DCS-002 | TS-R-04 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U3 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Soda Inlet | 17-XV-020211-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:9/ O1011102_U3:3 | TS-R-04:10/ O1011102_U3:4 |  |  | O1011102:3A/ O1011102_U3:5 | O1011102:3B/ O1011102_U3:6 | [6 empty] | 3A | 3B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020211 -A | 17XZSL020211A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.06 | 17-MC-DCS-002 | TS-R-04 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U4 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Soda Inlet | 17-XV-020211-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:11/ O1011102_U4:3 | TS-R-04:12/ O1011102_U4:4 |  |  | O1011102:4A/ O1011102_U4:5 | O1011102:4B/ O1011102_U4:6 | [6 empty] | 4A | 4B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020211 -A | 17XY020211A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.07 | 17-MC-DCS-002 | TS-O-05 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 32 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Soda Inlet | ВХОД СОДОВОЙ СМЕСИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:7/ O1011202:32A | TS-O-05:8/ O1011202:32C | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020211 -B | 17XZSH020211B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.05 | 17-MC-DCS-002 | TS-P-05 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U21 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Soda Inlet | 17-XV-020211-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:9/ O1011102_U21:3 | TS-P-05:10/ O1011102_U21:4 |  |  | O1011102:21A/ O1011102_U21:5 | O1011102:21B/ O1011102_U21:6 | [6 empty] | 21A | 21B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020211 -B | 17XZSL020211B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.06 | 17-MC-DCS-002 | TS-P-05 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U22 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Soda Inlet | 17-XV-020211-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:11/ O1011102_U22:3 | TS-P-05:12/ O1011102_U22:4 |  |  | O1011102:22A/ O1011102_U22:5 | O1011102:22B/ O1011102_U22:6 | [6 empty] | 22A | 22B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020211 -B | 17XY020211B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.05 | 17-MC-DCS-002 | TS-O-06 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 9 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Soda Inlet | ВХОД СОДОВОЙ СМЕСИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:5/ O1011203:9A | TS-O-06:6/ O1011203:9C | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020211 -C | 17XZSH020211C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.05 | 17-MC-DCS-002 | TS-Q-01 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U5 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Soda Inlet | 17-XV-020211-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:9/ O1011103_U5:3 | TS-Q-01:10/ O1011103_U5:4 |  |  | O1011103:5A/ O1011103_U5:5 | O1011103:5B/ O1011103_U5:6 | [6 empty] | 5A | 5B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020211 -C | 17XZSL020211C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.06 | 17-MC-DCS-002 | TS-Q-01 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U6 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Soda Inlet | 17-XV-020211-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:11/ O1011103_U6:3 | TS-Q-01:12/ O1011103_U6:4 |  |  | O1011103:6A/ O1011103_U6:5 | O1011103:6B/ O1011103_U6:6 | [6 empty] | 6A | 6B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020211 -C | 17XY020211C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.05 | 17-MC-DCS-002 | TS-P-01 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 20 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Soda Inlet | ВХОД СОДОВОЙ СМЕСИ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:5/ O1011203:20A | TS-P-01:6/ O1011203:20C | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020212 -A | 17XZSH020212A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.07 | 17-MC-DCS-002 | TS-R-04 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U5 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Acid Inlet / BW Inlet | 17-XV-020212-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:13/ O1011102_U5:3 | TS-R-04:14/ O1011102_U5:4 |  |  | O1011102:5A/ O1011102_U5:5 | O1011102:5B/ O1011102_U5:6 | [6 empty] | 5A | 5B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020212 -A | 17XZSL020212A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.08 | 17-MC-DCS-002 | TS-R-04 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U6 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Acid Inlet / BW Inlet | 17-XV-020212-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:15/ O1011102_U6:3 | TS-R-04:16/ O1011102_U6:4 |  |  | O1011102:6A/ O1011102_U6:5 | O1011102:6B/ O1011102_U6:6 | [6 empty] | 6A | 6B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020212 -A | 17XY020212A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.09 | 17-MC-DCS-002 | TS-O-05 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 1 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Acid Inlet / BW Inlet | ВХОД СМЕСИ КИСЛОТА/ПИТ ВОДА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:9/ O1011203:1A | TS-O-05:10/ O1011203:1C | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020212 -B | 17XZSH020212B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.07 | 17-MC-DCS-002 | TS-P-05 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U23 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Acid Inlet / BW Inlet | 17-XV-020212-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:13/ O1011102_U23:3 | TS-P-05:14/ O1011102_U23:4 |  |  | O1011102:23A/ O1011102_U23:5 | O1011102:23B/ O1011102_U23:6 | [6 empty] | 23A | 23B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020212 -B | 17XZSL020212B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.08 | 17-MC-DCS-002 | TS-P-05 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U24 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Acid Inlet / BW Inlet | 17-XV-020212-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:15/ O1011102_U24:3 | TS-P-05:16/ O1011102_U24:4 |  |  | O1011102:24A/ O1011102_U24:5 | O1011102:24B/ O1011102_U24:6 | [6 empty] | 24A | 24B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020212 -B | 17XY020212B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.07 | 17-MC-DCS-002 | TS-O-06 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 10 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Acid Inlet / BW Inlet | ВХОД СМЕСИ КИСЛОТА/ПИТ ВОДА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:7/ O1011203:10A | TS-O-06:8/ O1011203:10C | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020212 -C | 17XZSH020212C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.07 | 17-MC-DCS-002 | TS-Q-01 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U7 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Acid Inlet / BW Inlet | 17-XV-020212-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:13/ O1011103_U7:3 | TS-Q-01:14/ O1011103_U7:4 |  |  | O1011103:7A/ O1011103_U7:5 | O1011103:7B/ O1011103_U7:6 | [6 empty] | 7A | 7B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020212 -C | 17XZSL020212C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.08 | 17-MC-DCS-002 | TS-Q-01 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U8 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Acid Inlet / BW Inlet | 17-XV-020212-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:15/ O1011103_U8:3 | TS-Q-01:16/ O1011103_U8:4 |  |  | O1011103:8A/ O1011103_U8:5 | O1011103:8B/ O1011103_U8:6 | [6 empty] | 8A | 8B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020212 -C | 17XY020212C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.07 | 17-MC-DCS-002 | TS-P-01 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 21 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Acid Inlet / BW Inlet | ВХОД СМЕСИ КИСЛОТА/ПИТ ВОДА | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:7/ O1011203:21A | TS-P-01:8/ O1011203:21C | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020213 -A | 17XZSH020213A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.09 | 17-MC-DCS-002 | TS-R-04 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U7 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Inlet | 17-XV-020213-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:17/ O1011102_U7:3 | TS-R-04:18/ O1011102_U7:4 |  |  | O1011102:7A/ O1011102_U7:5 | O1011102:7B/ O1011102_U7:6 | [6 empty] | 7A | 7B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020213 -A | 17XZSL020213A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.10 | 17-MC-DCS-002 | TS-R-04 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U8 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Inlet | 17-XV-020213-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:19/ O1011102_U8:3 | TS-R-04:20/ O1011102_U8:4 |  |  | O1011102:8A/ O1011102_U8:5 | O1011102:8B/ O1011102_U8:6 | [6 empty] | 8A | 8B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020213 -A | 17XY020213A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.11 | 17-MC-DCS-002 | TS-O-05 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 2 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Inlet | ВХОД ВОЗДУХА В СМЕШАННЫЙ СЛОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:11/ O1011203:2A | TS-O-05:12/ O1011203:2C | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020213 -B | 17XZSH020213B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.09 | 17-MC-DCS-002 | TS-P-05 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U25 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Inlet | 17-XV-020213-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:17/ O1011102_U25:3 | TS-P-05:18/ O1011102_U25:4 |  |  | O1011102:25A/ O1011102_U25:5 | O1011102:25B/ O1011102_U25:6 | [6 empty] | 25A | 25B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020213 -B | 17XZSL020213B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.10 | 17-MC-DCS-002 | TS-P-05 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U26 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Inlet | 17-XV-020213-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:19/ O1011102_U26:3 | TS-P-05:20/ O1011102_U26:4 |  |  | O1011102:26A/ O1011102_U26:5 | O1011102:26B/ O1011102_U26:6 | [6 empty] | 26A | 26B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020213 -B | 17XY020213B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.09 | 17-MC-DCS-002 | TS-O-06 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 11 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Inlet | ВХОД ВОЗДУХА В СМЕШАННЫЙ СЛОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:9/ O1011203:11A | TS-O-06:10/ O1011203:11C | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020213 -C | 17XZSH020213C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.09 | 17-MC-DCS-002 | TS-Q-01 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U9 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Inlet | 17-XV-020213-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:17/ O1011103_U9:3 | TS-Q-01:18/ O1011103_U9:4 |  |  | O1011103:9A/ O1011103_U9:5 | O1011103:9B/ O1011103_U9:6 | [6 empty] | 9A | 9B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020213 -C | 17XZSL020213C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.10 | 17-MC-DCS-002 | TS-Q-01 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U10 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Inlet | 17-XV-020213-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:19/ O1011103_U10:3 | TS-Q-01:20/ O1011103_U10:4 |  |  | O1011103:10A/ O1011103_U10:5 | O1011103:10B/ O1011103_U10:6 | [6 empty] | 10A | 10B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020213 -C | 17XY020213C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.09 | 17-MC-DCS-002 | TS-P-01 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 22 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Air Inlet | ВХОД ВОЗДУХА В СМЕШАННЫЙ СЛОЙ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:9/ O1011203:22A | TS-P-01:10/ O1011203:22C | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020214 -A | 17XZSH020214A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.11 | 17-MC-DCS-002 | TS-R-04 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U9 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Outlet | 17-XV-020214-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:21/ O1011102_U9:3 | TS-R-04:22/ O1011102_U9:4 |  |  | O1011102:9A/ O1011102_U9:5 | O1011102:9B/ O1011102_U9:6 | [6 empty] | 9A | 9B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020214 -A | 17XZSL020214A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.12 | 17-MC-DCS-002 | TS-R-04 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U10 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Outlet | 17-XV-020214-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:23/ O1011102_U10:3 | TS-R-04:24/ O1011102_U10:4 |  |  | O1011102:10A/ O1011102_U10:5 | O1011102:10B/ O1011102_U10:6 | [6 empty] | 10A | 10B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020214 -A | 17XY020214A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.13 | 17-MC-DCS-002 | TS-O-05 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 3 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Outlet | ВЫХОД СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:13/ O1011203:3A | TS-O-05:14/ O1011203:3C | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020214 -B | 17XZSH020214B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.11 | 17-MC-DCS-002 | TS-P-05 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U27 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Outlet | 17-XV-020214-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:21/ O1011102_U27:3 | TS-P-05:22/ O1011102_U27:4 |  |  | O1011102:27A/ O1011102_U27:5 | O1011102:27B/ O1011102_U27:6 | [6 empty] | 27A | 27B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020214 -B | 17XZSL020214B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.12 | 17-MC-DCS-002 | TS-P-05 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U28 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Outlet | 17-XV-020214-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:23/ O1011102_U28:3 | TS-P-05:24/ O1011102_U28:4 |  |  | O1011102:28A/ O1011102_U28:5 | O1011102:28B/ O1011102_U28:6 | [6 empty] | 28A | 28B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020214 -B | 17XY020214B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.11 | 17-MC-DCS-002 | TS-O-06 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 12 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Outlet | ВЫХОД СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:11/ O1011203:12A | TS-O-06:12/ O1011203:12C | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020214 -C | 17XZSH020214C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.11 | 17-MC-DCS-002 | TS-Q-01 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U11 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Outlet | 17-XV-020214-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:21/ O1011103_U11:3 | TS-Q-01:22/ O1011103_U11:4 |  |  | O1011103:11A/ O1011103_U11:5 | O1011103:11B/ O1011103_U11:6 | [6 empty] | 11A | 11B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020214 -C | 17XZSL020214C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.12 | 17-MC-DCS-002 | TS-Q-01 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U12 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Outlet | 17-XV-020214-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:23/ O1011103_U12:3 | TS-Q-01:24/ O1011103_U12:4 |  |  | O1011103:12A/ O1011103_U12:5 | O1011103:12B/ O1011103_U12:6 | [6 empty] | 12A | 12B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020214 -C | 17XY020214C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.11 | 17-MC-DCS-002 | TS-P-01 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 23 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Outlet | ВЫХОД СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:11/ O1011203:23A | TS-P-01:12/ O1011203:23C | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020215 -A | 17XZSH020215A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.13 | 17-MC-DCS-002 | TS-R-04 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U11 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Drain | 17-XV-020215-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:25/ O1011102_U11:3 | TS-R-04:26/ O1011102_U11:4 |  |  | O1011102:11A/ O1011102_U11:5 | O1011102:11B/ O1011102_U11:6 | [6 empty] | 11A | 11B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020215 -A | 17XZSL020215A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.14 | 17-MC-DCS-002 | TS-R-04 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U12 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Drain | 17-XV-020215-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:27/ O1011102_U12:3 | TS-R-04:28/ O1011102_U12:4 |  |  | O1011102:12A/ O1011102_U12:5 | O1011102:12B/ O1011102_U12:6 | [6 empty] | 12A | 12B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020215 -A | 17XY020215A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.15 | 17-MC-DCS-002 | TS-O-05 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 4 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Drain | ДРЕНАЖ СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:15/ O1011203:4A | TS-O-05:16/ O1011203:4C | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020215 -B | 17XZSH020215B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.13 | 17-MC-DCS-002 | TS-P-05 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U29 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Drain | 17-XV-020215-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:25/ O1011102_U29:3 | TS-P-05:26/ O1011102_U29:4 |  |  | O1011102:29A/ O1011102_U29:5 | O1011102:29B/ O1011102_U29:6 | [6 empty] | 29A | 29B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020215 -B | 17XZSL020215B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.14 | 17-MC-DCS-002 | TS-P-05 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U30 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Drain | 17-XV-020215-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:27/ O1011102_U30:3 | TS-P-05:28/ O1011102_U30:4 |  |  | O1011102:30A/ O1011102_U30:5 | O1011102:30B/ O1011102_U30:6 | [6 empty] | 30A | 30B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020215 -B | 17XY020215B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.13 | 17-MC-DCS-002 | TS-O-06 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 13 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Drain | ДРЕНАЖ СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:13/ O1011203:13A | TS-O-06:14/ O1011203:13C | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020215 -C | 17XZSH020215C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.13 | 17-MC-DCS-002 | TS-Q-01 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U13 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Drain | 17-XV-020215-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:25/ O1011103_U13:3 | TS-Q-01:26/ O1011103_U13:4 |  |  | O1011103:13A/ O1011103_U13:5 | O1011103:13B/ O1011103_U13:6 | [6 empty] | 13A | 13B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020215 -C | 17XZSL020215C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.14 | 17-MC-DCS-002 | TS-Q-01 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U14 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Drain | 17-XV-020215-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:27/ O1011103_U14:3 | TS-Q-01:28/ O1011103_U14:4 |  |  | O1011103:14A/ O1011103_U14:5 | O1011103:14B/ O1011103_U14:6 | [6 empty] | 14A | 14B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020215 -C | 17XY020215C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.13 | 17-MC-DCS-002 | TS-P-01 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 24 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Drain | ДРЕНАЖ СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:13/ O1011203:24A | TS-P-01:14/ O1011203:24C | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020216 -A | 17XZSH020216A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.15 | 17-MC-DCS-002 | TS-R-04 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U13 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Rinse Outlet | 17-XV-020216-A ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:29/ O1011102_U13:3 | TS-R-04:30/ O1011102_U13:4 |  |  | O1011102:13A/ O1011102_U13:5 | O1011102:13B/ O1011102_U13:6 | [6 empty] | 13A | 13B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020216 -A | 17XZSL020216A |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-004FL03-L022 | 24 Pair | Pr.16 | 17-MC-DCS-002 | TS-R-04 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U14 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Rinse Outlet | 17-XV-020216-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-04:31/ O1011102_U14:3 | TS-R-04:32/ O1011102_U14:4 |  |  | O1011102:14A/ O1011102_U14:5 | O1011102:14B/ O1011102_U14:6 | [6 empty] | 14A | 14B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020216 -A | 17XY020216A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-004FL03-L022 | 30 Core | C.17 | 17-MC-DCS-002 | TS-O-05 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 5 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Rinse Outlet | ВЫХОД ПРОМЫВКИ СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-05:17/ O1011203:5A | TS-O-05:18/ O1011203:5C | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020216 -B | 17XZSH020216B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.15 | 17-MC-DCS-002 | TS-P-05 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U31 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Rinse Outlet | 17-XV-020216-B ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:29/ O1011102_U31:3 | TS-P-05:30/ O1011102_U31:4 |  |  | O1011102:31A/ O1011102_U31:5 | O1011102:31B/ O1011102_U31:6 | [6 empty] | 31A | 31B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020216 -B | 17XZSL020216B |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-005FL03-L022 | 24 Pair | Pr.16 | 17-MC-DCS-002 | TS-P-05 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011102_U32 | HD5516 | O1011102 | TUA711-DIO32 | 17-SC-DCS-002/O1011102/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011102 | 3 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Rinse Outlet | 17-XV-020216-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-05:31/ O1011102_U32:3 | TS-P-05:32/ O1011102_U32:4 |  |  | O1011102:32A/ O1011102_U32:5 | O1011102:32B/ O1011102_U32:6 | [6 empty] | 32A | 32B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020216 -B | 17XY020216B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-005FL03-L022 | 30 Core | C.15 | 17-MC-DCS-002 | TS-O-06 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 14 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Rinse Outlet | ВЫХОД ПРОМЫВКИ СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-O-06:15/ O1011203:14A | TS-O-06:16/ O1011203:14C | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020216 -C | 17XZSH020216C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.15 | 17-MC-DCS-002 | TS-Q-01 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U15 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Rinse Outlet | 17-XV-020216-C ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:29/ O1011103_U15:3 | TS-Q-01:30/ O1011103_U15:4 |  |  | O1011103:15A/ O1011103_U15:5 | O1011103:15B/ O1011103_U15:6 | [6 empty] | 15A | 15B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020216 -C | 17XZSL020216C |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-N-006FL03-L022 | 24 Pair | Pr.16 | 17-MC-DCS-002 | TS-Q-01 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U16 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Rinse Outlet | 17-XV-020216-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-01:31/ O1011103_U16:3 | TS-Q-01:32/ O1011103_U16:4 |  |  | O1011103:16A/ O1011103_U16:5 | O1011103:16B/ O1011103_U16:6 | [6 empty] | 16A | 16B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020216 -C | 17XY020216C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL03-L022 | 30 Core | C.15 | 17-MC-DCS-002 | TS-P-01 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 25 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Mixed Bed Rinse Outlet | ВЫХОД ПРОМЫВКИ СМЕШАННОГО СЛОЯ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-01:15/ O1011203:25A | TS-P-01:16/ O1011203:25C | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020217 | 17XZSH020217 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-02 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U17 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 from metering pumps | 17XV020217 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:1/ O1011103_U17:3 | TS-Q-02:2/ O1011103_U17:4 |  |  | O1011103:17A/ O1011103_U17:5 | O1011103:17B/ O1011103_U17:6 | [6 empty] | 17A | 17B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020217 | 17XZSL020217 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.02 | 17-MC-DCS-002 | TS-Q-02 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U18 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 from metering pumps | 17XV020217 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:3/ O1011103_U18:3 | TS-Q-02:4/ O1011103_U18:4 |  |  | O1011103:18A/ O1011103_U18:5 | O1011103:18B/ O1011103_U18:6 | [6 empty] | 18A | 18B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020217 | 17XY020217 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DO_01 | Field |  | 17-C-CD-N-007FL03-L022 | 30 Core | C.01 | 17-MC-DCS-002 | TS-P-03 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 31 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | H2SO4 from metering pumps | H2SO4 ИЗ ДОЗИРУЮЩИХ НАСОСОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-03:1/ O1011203:31A | TS-P-03:2/ O1011203:31C | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020218 | 17XZSH020218 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.03 | 17-MC-DCS-002 | TS-Q-02 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U19 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 to regeneration | 17XV020218 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:5/ O1011103_U19:3 | TS-Q-02:6/ O1011103_U19:4 |  |  | O1011103:19A/ O1011103_U19:5 | O1011103:19B/ O1011103_U19:6 | [6 empty] | 19A | 19B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020218 | 17XZSL020218 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.04 | 17-MC-DCS-002 | TS-Q-02 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U20 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 to regeneration | 17XV020218 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:7/ O1011103_U20:3 | TS-Q-02:8/ O1011103_U20:4 |  |  | O1011103:20A/ O1011103_U20:5 | O1011103:20B/ O1011103_U20:6 | [6 empty] | 20A | 20B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020218 | 17XY020218 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DO_01 | Field |  | 17-C-CD-N-007FL03-L022 | 30 Core | C.03 | 17-MC-DCS-002 | TS-P-03 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011203 | TUA711-DOR32 | 17-SC-DCS-002/O1011203/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011203 | 4 | 32 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | H2SO4 to regeneration | H2SO4 В РЕГЕНЕРАЦИЮ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-03:3/ O1011203:32A | TS-P-03:4/ O1011203:32C | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020219 | 17XZSH020219 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.05 | 17-MC-DCS-002 | TS-Q-02 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U21 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 to regeneration, drain | 17XV020219 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:9/ O1011103_U21:3 | TS-Q-02:10/ O1011103_U21:4 |  |  | O1011103:21A/ O1011103_U21:5 | O1011103:21B/ O1011103_U21:6 | [6 empty] | 21A | 21B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020219 | 17XZSL020219 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.06 | 17-MC-DCS-002 | TS-Q-02 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U22 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 to regeneration, drain | 17XV020219 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:11/ O1011103_U22:3 | TS-Q-02:12/ O1011103_U22:4 |  |  | O1011103:22A/ O1011103_U22:5 | O1011103:22B/ O1011103_U22:6 | [6 empty] | 22A | 22B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020219 | 17XY020219 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DO_01 | Field |  | 17-C-CD-N-007FL03-L022 | 30 Core | C.05 | 17-MC-DCS-002 | TS-P-03 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 13 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | H2SO4 to regeneration, drain | H2SO4 В РЕГЕНЕРАЦИЮ, СЛИВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-03:5/ O1011204:13A | TS-P-03:6/ O1011204:13C | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020220 | 17XZSH020220 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.07 | 17-MC-DCS-002 | TS-Q-02 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U23 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH from metering pumps | 17XV020220 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:13/ O1011103_U23:3 | TS-Q-02:14/ O1011103_U23:4 |  |  | O1011103:23A/ O1011103_U23:5 | O1011103:23B/ O1011103_U23:6 | [6 empty] | 23A | 23B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020220 | 17XZSL020220 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.08 | 17-MC-DCS-002 | TS-Q-02 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U24 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH from metering pumps | 17XV020220 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:15/ O1011103_U24:3 | TS-Q-02:16/ O1011103_U24:4 |  |  | O1011103:24A/ O1011103_U24:5 | O1011103:24B/ O1011103_U24:6 | [6 empty] | 24A | 24B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020220 | 17XY020220 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DO_01 | Field |  | 17-C-CD-N-007FL03-L022 | 30 Core | C.07 | 17-MC-DCS-002 | TS-P-03 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 14 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | NaOH from metering pumps | NAOH ИЗ ДОЗИРУЮЩИХ НАСОСОВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-03:7/ O1011204:14A | TS-P-03:8/ O1011204:14C | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020221 | 17XZSH020221 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.09 | 17-MC-DCS-002 | TS-Q-02 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U25 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH to regeneration | 17XV020221 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:17/ O1011103_U25:3 | TS-Q-02:18/ O1011103_U25:4 |  |  | O1011103:25A/ O1011103_U25:5 | O1011103:25B/ O1011103_U25:6 | [6 empty] | 25A | 25B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020221 | 17XZSL020221 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.10 | 17-MC-DCS-002 | TS-Q-02 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U26 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH to regeneration | 17XV020221 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:19/ O1011103_U26:3 | TS-Q-02:20/ O1011103_U26:4 |  |  | O1011103:26A/ O1011103_U26:5 | O1011103:26B/ O1011103_U26:6 | [6 empty] | 26A | 26B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020221 | 17XY020221 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DO_01 | Field |  | 17-C-CD-N-007FL03-L022 | 30 Core | C.09 | 17-MC-DCS-002 | TS-P-03 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 15 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | NaOH to regeneration | NAOH В РЕГЕНЕРАЦИЮ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-03:9/ O1011204:15A | TS-P-03:10/ O1011204:15C | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020222 | 17XZSH020222 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.11 | 17-MC-DCS-002 | TS-Q-02 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U27 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH to regeneration, drain | 17XV020222 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:21/ O1011103_U27:3 | TS-Q-02:22/ O1011103_U27:4 |  |  | O1011103:27A/ O1011103_U27:5 | O1011103:27B/ O1011103_U27:6 | [6 empty] | 27A | 27B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020222 | 17XZSL020222 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DI_02 | Field |  | 17-C-DD-N-007FL03-L022 | 24 Pair | Pr.12 | 17-MC-DCS-002 | TS-Q-02 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U28 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH to regeneration, drain | 17XV020222 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:23/ O1011103_U28:3 | TS-Q-02:24/ O1011103_U28:4 |  |  | O1011103:28A/ O1011103_U28:5 | O1011103:28B/ O1011103_U28:6 | [6 empty] | 28A | 28B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020222 | 17XY020222 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.4 | DCS_DO_01 | Field |  | 17-C-CD-N-007FL03-L022 | 30 Core | C.11 | 17-MC-DCS-002 | TS-P-03 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 16 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | NaOH to regeneration, drain | NAOH В РЕГЕНЕРАЦИЮ, СЛИВ | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-03:11/ O1011204:16A | TS-P-03:12/ O1011204:16C | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020224 | 17XZSH020224 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-03 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U29 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH to neutralization basin 022A | 11-XV-020224 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:1/ O1011103_U29:3 | TS-Q-03:2/ O1011103_U29:4 |  |  | O1011103:29A/ O1011103_U29:5 | O1011103:29B/ O1011103_U29:6 | [6 empty] | 29A | 29B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020224 | 17XZSL020224 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.02 | 17-MC-DCS-002 | TS-Q-03 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U30 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH to neutralization basin 022A | 11-XV-020224 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:3/ O1011103_U30:3 | TS-Q-03:4/ O1011103_U30:4 |  |  | O1011103:30A/ O1011103_U30:5 | O1011103:30B/ O1011103_U30:6 | [6 empty] | 30A | 30B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020224 | 17XY020224 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-009FL03-L022 | 30 Core | C.01 | 17-MC-DCS-001 | TS-H-05 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 3 | DO716-S11 | 32 | 0.25 | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | NaOH to neutralization basin 022A | NAOH В БАСЕЙН НЕЙТР 022A | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:1/ O1011212:3A | TS-H-05:2/ O1011212:3C | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020225 | 17XZSH020225 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.03 | 17-MC-DCS-002 | TS-Q-03 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U31 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 to neutralization basin 022A | 11-XV-020225 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:5/ O1011103_U31:3 | TS-Q-03:6/ O1011103_U31:4 |  |  | O1011103:31A/ O1011103_U31:5 | O1011103:31B/ O1011103_U31:6 | [6 empty] | 31A | 31B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020225 | 17XZSL020225 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.04 | 17-MC-DCS-002 | TS-Q-03 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011103_U32 | HD5516 | O1011103 | TUA711-DIO32 | 17-SC-DCS-002/O1011103/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011103 | 4 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 to neutralization basin 022A | 11-XV-020225 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:7/ O1011103_U32:3 | TS-Q-03:8/ O1011103_U32:4 |  |  | O1011103:32A/ O1011103_U32:5 | O1011103:32B/ O1011103_U32:6 | [6 empty] | 32A | 32B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020225 | 17XY020225 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-009FL03-L022 | 30 Core | C.03 | 17-MC-DCS-001 | TS-H-05 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 4 | DO716-S11 | 32 | 0.25 | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | H2SO4 to neutralization basin 022A | H2SO4 В БАСЕЙН НЕЙТР 022A | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:3/ O1011212:4A | TS-H-05:4/ O1011212:4C | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020226 | 17XZSH020226 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.05 | 17-MC-DCS-002 | TS-Q-03 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U6 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH to neutralization basin 022B | 11-XV-020226 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:9/ O1011104_U6:3 | TS-Q-03:10/ O1011104_U6:4 |  |  | O1011104:6A/ O1011104_U6:5 | O1011104:6B/ O1011104_U6:6 | [6 empty] | 6A | 6B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020226 | 17XZSL020226 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.06 | 17-MC-DCS-002 | TS-Q-03 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U7 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | NaOH to neutralization basin 022B | 11-XV-020226 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:11/ O1011104_U7:3 | TS-Q-03:12/ O1011104_U7:4 |  |  | O1011104:7A/ O1011104_U7:5 | O1011104:7B/ O1011104_U7:6 | [6 empty] | 7A | 7B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020226 | 17XY020226 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-009FL03-L022 | 30 Core | C.05 | 17-MC-DCS-001 | TS-H-05 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 5 | DO716-S11 | 32 | 0.25 | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | NaOH to neutralization basin 022B | NAOH В БАСЕЙН НЕЙТР 022B | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:5/ O1011212:5A | TS-H-05:6/ O1011212:5C | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020227 | 17XZSH020227 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.07 | 17-MC-DCS-002 | TS-Q-03 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U8 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 to neutralization basin 022B | 11-XV-020227 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:13/ O1011104_U8:3 | TS-Q-03:14/ O1011104_U8:4 |  |  | O1011104:8A/ O1011104_U8:5 | O1011104:8B/ O1011104_U8:6 | [6 empty] | 8A | 8B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020227 | 17XZSL020227 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.08 | 17-MC-DCS-002 | TS-Q-03 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U9 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | H2SO4 to neutralization basin 022B | 11-XV-020227 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:15/ O1011104_U9:3 | TS-Q-03:16/ O1011104_U9:4 |  |  | O1011104:9A/ O1011104_U9:5 | O1011104:9B/ O1011104_U9:6 | [6 empty] | 9A | 9B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020227 | 17XY020227 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-009FL03-L022 | 30 Core | C.07 | 17-MC-DCS-001 | TS-H-05 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 6 | DO716-S11 | 32 | 0.25 | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | H2SO4 to neutralization basin 022B | H2SO4 В БАСЕЙН НЕЙТР 022B | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:7/ O1011212:6A | TS-H-05:8/ O1011212:6C | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020228 | 17XZSH020228 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-010FL03-L022 | 12 Pair | Pr.01 | 17-MC-DCS-002 | TS-Q-04 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011104_U18 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022A recirculation valve | 11-XV-020228 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:1/ O1011104_U18:3 | TS-Q-04:2/ O1011104_U18:4 |  |  | O1011104:18A/ O1011104_U18:5 | O1011104:18B/ O1011104_U18:6 | [6 empty] | 18A | 18B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020228 | 17XZSL020228 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-010FL03-L022 | 12 Pair | Pr.02 | 17-MC-DCS-002 | TS-Q-04 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011104_U19 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022A recirculation valve | 11-XV-020228 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:3/ O1011104_U19:3 | TS-Q-04:4/ O1011104_U19:4 |  |  | O1011104:19A/ O1011104_U19:5 | O1011104:19B/ O1011104_U19:6 | [6 empty] | 19A | 19B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020228 | 17XY020228 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-010FL03-L022 | 30 Core | C.01 | 17-MC-DCS-002 | TS-P-04 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 19 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022A recirculation valve | БАСЕЙН НЕЙТРАЛИЗАЦИИ 022A РЕЦИРК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-04:1/ O1011204:19A | TS-P-04:2/ O1011204:19C | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020229 | 17XZSH020229 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-010FL03-L022 | 12 Pair | Pr.03 | 17-MC-DCS-002 | TS-Q-04 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011104_U20 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022A outlet valve | 11-XV-020229 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:5/ O1011104_U20:3 | TS-Q-04:6/ O1011104_U20:4 |  |  | O1011104:20A/ O1011104_U20:5 | O1011104:20B/ O1011104_U20:6 | [6 empty] | 20A | 20B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020229 | 17XZSL020229 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-010FL03-L022 | 12 Pair | Pr.04 | 17-MC-DCS-002 | TS-Q-04 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011104_U21 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022A outlet valve | 11-XV-020229 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:7/ O1011104_U21:3 | TS-Q-04:8/ O1011104_U21:4 |  |  | O1011104:21A/ O1011104_U21:5 | O1011104:21B/ O1011104_U21:6 | [6 empty] | 21A | 21B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020229 | 17XY020229 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-010FL03-L022 | 30 Core | C.03 | 17-MC-DCS-002 | TS-P-04 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 20 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022A outlet valve | ВЫХОД БАСЕЙНА НЕЙТРАЛИЗАЦИИ 022A | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-04:3/ O1011204:20A | TS-P-04:4/ O1011204:20C | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020230 | 17XZSH020230 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-010FL03-L022 | 12 Pair | Pr.05 | 17-MC-DCS-002 | TS-Q-04 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011104_U22 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022B outlet valve | 11-XV-020230 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:9/ O1011104_U22:3 | TS-Q-04:10/ O1011104_U22:4 |  |  | O1011104:22A/ O1011104_U22:5 | O1011104:22B/ O1011104_U22:6 | [6 empty] | 22A | 22B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020230 | 17XZSL020230 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-010FL03-L022 | 12 Pair | Pr.06 | 17-MC-DCS-002 | TS-Q-04 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011104_U23 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022B outlet valve | 11-XV-020230 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:11/ O1011104_U23:3 | TS-Q-04:12/ O1011104_U23:4 |  |  | O1011104:23A/ O1011104_U23:5 | O1011104:23B/ O1011104_U23:6 | [6 empty] | 23A | 23B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020230 | 17XY020230 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-010FL03-L022 | 30 Core | C.05 | 17-MC-DCS-002 | TS-P-04 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 21 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022B outlet valve | ВЫХОД БАСЕЙНА НЕЙТРАЛИЗАЦИИ 022B | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-04:5/ O1011204:21A | TS-P-04:6/ O1011204:21C | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020231 | 17XZSH020231 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-010FL03-L022 | 12 Pair | Pr.07 | 17-MC-DCS-002 | TS-Q-04 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011104_U24 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022B recirculation valve | 11-XV-020231 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:13/ O1011104_U24:3 | TS-Q-04:14/ O1011104_U24:4 |  |  | O1011104:24A/ O1011104_U24:5 | O1011104:24B/ O1011104_U24:6 | [6 empty] | 24A | 24B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020231 | 17XZSL020231 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-010FL03-L022 | 12 Pair | Pr.08 | 17-MC-DCS-002 | TS-Q-04 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1011104_U25 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022B recirculation valve | 11-XV-020231 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-04:15/ O1011104_U25:3 | TS-Q-04:16/ O1011104_U25:4 |  |  | O1011104:25A/ O1011104_U25:5 | O1011104:25B/ O1011104_U25:6 | [6 empty] | 25A | 25B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020231 | 17XY020231 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-010FL03-L022 | 30 Core | C.07 | 17-MC-DCS-002 | TS-P-04 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 22 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Neutralization basin 022B recirculation valve | БАСЕЙН НЕЙТРАЛИЗАЦИИ 022B РЕЦИРК | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-04:7/ O1011204:22A | TS-P-04:8/ O1011204:22C | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020232 | 17XZSH020232 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.13 | 17-MC-DCS-002 | TS-Q-03 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U14 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From SAC to neutralization basin 022A | 11-XV-020232 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:25/ O1011104_U14:3 | TS-Q-03:26/ O1011104_U14:4 |  |  | O1011104:14A/ O1011104_U14:5 | O1011104:14B/ O1011104_U14:6 | [6 empty] | 14A | 14B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020232 | 17XZSL020232 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.14 | 17-MC-DCS-002 | TS-Q-03 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U15 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From SAC to neutralization basin 022A | 11-XV-020232 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:27/ O1011104_U15:3 | TS-Q-03:28/ O1011104_U15:4 |  |  | O1011104:15A/ O1011104_U15:5 | O1011104:15B/ O1011104_U15:6 | [6 empty] | 15A | 15B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020232 | 17XY020232 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-009FL03-L022 | 30 Core | C.13 | 17-MC-DCS-001 | TS-H-05 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 7 | DO716-S11 | 32 | 0.25 | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | From SAC to neutralization basin 022A | ИЗ ФИЛЬТРА В БАССЕЙН НЕЙТР 022А | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:13/ O1011212:7A | TS-H-05:14/ O1011212:7C | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020233 | 17XZSH020233 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.15 | 17-MC-DCS-002 | TS-Q-03 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U16 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From SAC to neutralization basin 022B | 11-XV-020233 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:29/ O1011104_U16:3 | TS-Q-03:30/ O1011104_U16:4 |  |  | O1011104:16A/ O1011104_U16:5 | O1011104:16B/ O1011104_U16:6 | [6 empty] | 16A | 16B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020233 | 17XZSL020233 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.16 | 17-MC-DCS-002 | TS-Q-03 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U17 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From SAC to neutralization basin 022B | 11-XV-020233 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:31/ O1011104_U17:3 | TS-Q-03:32/ O1011104_U17:4 |  |  | O1011104:17A/ O1011104_U17:5 | O1011104:17B/ O1011104_U17:6 | [6 empty] | 17A | 17B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020233 | 17XY020233 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-009FL03-L022 | 30 Core | C.15 | 17-MC-DCS-001 | TS-H-05 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 8 | DO716-S11 | 32 | 0.25 | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | From SAC to neutralization basin 022B | ИЗ ФИЛЬТРА В БАССЕЙН НЕЙТР 022В | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:15/ O1011212:8A | TS-H-05:16/ O1011212:8C | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020250 | 17XZSH020250 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.09 | 17-MC-DCS-002 | TS-Q-03 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U10 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Steam to neutralization basin 022A | 17-XV-020250 Открыто | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:17/ O1011104_U10:3 | TS-Q-03:18/ O1011104_U10:4 |  |  | O1011104:10A/ O1011104_U10:5 | O1011104:10B/ O1011104_U10:6 | [6 empty] | 10A | 10B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020250 | 17XZSL020250 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.10 | 17-MC-DCS-002 | TS-Q-03 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U11 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Steam to neutralization basin 022A | 17-XV-020250 Закрыто | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:19/ O1011104_U11:3 | TS-Q-03:20/ O1011104_U11:4 |  |  | O1011104:11A/ O1011104_U11:5 | O1011104:11B/ O1011104_U11:6 | [6 empty] | 11A | 11B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020250 | 17XY020250 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-009FL03-L022 | 30 Core | C.09 | 17-MC-DCS-001 | TS-H-05 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 1 | DO716-S11 | 32 | 0.25 | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | Steam to neutralization basin 022A | Пар в сборник нейтр 17-L-022-BS-022A | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:9/ O1011212:1A | TS-H-05:10/ O1011212:1C | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020251 | 17XZSH020251 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.11 | 17-MC-DCS-002 | TS-Q-03 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U12 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Steam to neutralization basin 022B | 17-XV-020251 Открыто | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:21/ O1011104_U12:3 | TS-Q-03:22/ O1011104_U12:4 |  |  | O1011104:12A/ O1011104_U12:5 | O1011104:12B/ O1011104_U12:6 | [6 empty] | 12A | 12B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020251 | 17XZSL020251 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DI_02 | Field |  | 17-C-DD-N-009FL03-L022 | 24 Pair | Pr.12 | 17-MC-DCS-002 | TS-Q-03 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U13 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Steam to neutralization basin 022B | 17-XV-020251 Закрыто | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-03:23/ O1011104_U13:3 | TS-Q-03:24/ O1011104_U13:4 |  |  | O1011104:13A/ O1011104_U13:5 | O1011104:13B/ O1011104_U13:6 | [6 empty] | 13A | 13B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -020251 | 17XY020251 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-FY-VD-BD17617L02200002_SH.7 | DCS_DO_01 | Field |  | 17-C-CD-N-009FL03-L022 | 30 Core | C.11 | 17-MC-DCS-001 | TS-H-05 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 2 | DO716-S11 | 32 | 0.25 | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | Steam to neutralization basin 022B | Пар в сборник нейтр 17-L-022-BS-022A | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-05:11/ O1011212:2A | TS-H-05:12/ O1011212:2C | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03021 | 17XZSH03021 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.01 | 17-MC-DCS-001 | TS-F-06 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U8 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | 17-XV-03021 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:1/ O1010203_U8:3 | TS-F-06:2/ O1010203_U8:4 |  |  | O1010203:8A/ O1010203_U8:5 | O1010203:8B/ O1010203_U8:6 | [6 empty] | 8A | 8B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03021 | 17XZSL03021 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.02 | 17-MC-DCS-001 | TS-F-06 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U9 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | 17-XV-03021 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:3/ O1010203_U9:3 | TS-F-06:4/ O1010203_U9:4 |  |  | O1010203:9A/ O1010203_U9:5 | O1010203:9B/ O1010203_U9:6 | [6 empty] | 9A | 9B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03021 | 17XY03021 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703004 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.01 | 17-MC-DCS-001 | TS-G-04 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 27 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | КОНДЕНСАТ ПАРА В 17T030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:1/ O1010210:27A | TS-G-04:2/ O1010210:27C | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03022 | 17XZSH03022 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.03 | 17-MC-DCS-001 | TS-F-06 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U10 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | 17-XV-03022 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:5/ O1010203_U10:3 | TS-F-06:6/ O1010203_U10:4 |  |  | O1010203:10A/ O1010203_U10:5 | O1010203:10B/ O1010203_U10:6 | [6 empty] | 10A | 10B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03022 | 17XZSL03022 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.04 | 17-MC-DCS-001 | TS-F-06 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U11 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | 17-XV-03022 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:7/ O1010203_U11:3 | TS-F-06:8/ O1010203_U11:4 |  |  | O1010203:11A/ O1010203_U11:5 | O1010203:11B/ O1010203_U11:6 | [6 empty] | 11A | 11B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03022 | 17XY03022 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703004 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.03 | 17-MC-DCS-001 | TS-G-04 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 28 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | КОНДЕНСАТ ПАРА В 17T030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:3/ O1010210:28A | TS-G-04:4/ O1010210:28C | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03023 | 17XZSH03023 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.05 | 17-MC-DCS-001 | TS-F-06 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U12 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | 17-XV-03023 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:9/ O1010203_U12:3 | TS-F-06:10/ O1010203_U12:4 |  |  | O1010203:12A/ O1010203_U12:5 | O1010203:12B/ O1010203_U12:6 | [6 empty] | 12A | 12B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03023 | 17XZSL03023 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.06 | 17-MC-DCS-001 | TS-F-06 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U13 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | 17-XV-03023 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:11/ O1010203_U13:3 | TS-F-06:12/ O1010203_U13:4 |  |  | O1010203:13A/ O1010203_U13:5 | O1010203:13B/ O1010203_U13:6 | [6 empty] | 13A | 13B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03023 | 17XY03023 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703004 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.05 | 17-MC-DCS-001 | TS-G-04 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 29 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | КОНДЕНСАТ ПАРА В 17T030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:5/ O1010210:29A | TS-G-04:6/ O1010210:29C | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03024 | 17XZSH03024 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.07 | 17-MC-DCS-001 | TS-F-06 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U14 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | 17-XV-03024 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:13/ O1010203_U14:3 | TS-F-06:14/ O1010203_U14:4 |  |  | O1010203:14A/ O1010203_U14:5 | O1010203:14B/ O1010203_U14:6 | [6 empty] | 14A | 14B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03024 | 17XZSL03024 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.08 | 17-MC-DCS-001 | TS-F-06 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U15 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | 17-XV-03024 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:15/ O1010203_U15:3 | TS-F-06:16/ O1010203_U15:4 |  |  | O1010203:15A/ O1010203_U15:5 | O1010203:15B/ O1010203_U15:6 | [6 empty] | 15A | 15B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03024 | 17XY03024 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703004 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.07 | 17-MC-DCS-001 | TS-G-04 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 30 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Turbine Steam Condensate to 17-T-030 | КОНДЕНСАТ ПАРА В 17T030 | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:7/ O1010210:30A | TS-G-04:8/ O1010210:30C | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03025 | 17XZSH03025 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.09 | 17-MC-DCS-001 | TS-F-06 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U16 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-030A discharge line | 17-XV-03025 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:17/ O1010203_U16:3 | TS-F-06:18/ O1010203_U16:4 |  |  | O1010203:16A/ O1010203_U16:5 | O1010203:16B/ O1010203_U16:6 | [6 empty] | 16A | 16B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03025 | 17XZSL03025 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.10 | 17-MC-DCS-001 | TS-F-06 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U17 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-030A discharge line | 17-XV-03025 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:19/ O1010203_U17:3 | TS-F-06:20/ O1010203_U17:4 |  |  | O1010203:17A/ O1010203_U17:5 | O1010203:17B/ O1010203_U17:6 | [6 empty] | 17A | 17B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03025 | 17XY03025 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703004 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.09 | 17-MC-DCS-001 | TS-G-04 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 31 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | 17-P-030A discharge line | ЛИНИЯ НАГНЕТАНИЯ 17-P-030A | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:9/ O1010210:31A | TS-G-04:10/ O1010210:31C | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03026 | 17XZSH03026 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.11 | 17-MC-DCS-001 | TS-F-06 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U18 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-030B discharge line | 17-XV-03026 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:21/ O1010203_U18:3 | TS-F-06:22/ O1010203_U18:4 |  |  | O1010203:18A/ O1010203_U18:5 | O1010203:18B/ O1010203_U18:6 | [6 empty] | 18A | 18B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03026 | 17XZSL03026 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.12 | 17-MC-DCS-001 | TS-F-06 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U19 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-030B discharge line | 17-XV-03026 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:23/ O1010203_U19:3 | TS-F-06:24/ O1010203_U19:4 |  |  | O1010203:19A/ O1010203_U19:5 | O1010203:19B/ O1010203_U19:6 | [6 empty] | 19A | 19B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03026 | 17XY03026 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703004 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.11 | 17-MC-DCS-001 | TS-G-04 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 32 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | 17-P-030B discharge line | ЛИНИЯ НАГНЕТАНИЯ 17-P-030В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:11/ O1010210:32A | TS-G-04:12/ O1010210:32C | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03027 | 17XZSH03027 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.13 | 17-MC-DCS-001 | TS-F-06 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U20 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-030C discharge line | 17-XV-03027 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:25/ O1010203_U20:3 | TS-F-06:26/ O1010203_U20:4 |  |  | O1010203:20A/ O1010203_U20:5 | O1010203:20B/ O1010203_U20:6 | [6 empty] | 20A | 20B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03027 | 17XZSL03027 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.14 | 17-MC-DCS-001 | TS-F-06 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U21 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-030C discharge line | 17-XV-03027 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:27/ O1010203_U21:3 | TS-F-06:28/ O1010203_U21:4 |  |  | O1010203:21A/ O1010203_U21:5 | O1010203:21B/ O1010203_U21:6 | [6 empty] | 21A | 21B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03027 | 17XY03027 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703004 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.13 | 17-MC-DCS-001 | TS-G-04 | 13 | 14 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 1 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | 17-P-030C discharge line | ЛИНИЯ НАГНЕТАНИЯ 17-P-030С | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:13/ O1010211:1A | TS-G-04:14/ O1010211:1C | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03059 | 17XZSH03059 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703003 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.15 | 17-MC-DCS-001 | TS-F-06 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U22 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-031A discharge line | 17-XV-03059 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:29/ O1010203_U22:3 | TS-F-06:30/ O1010203_U22:4 |  |  | O1010203:22A/ O1010203_U22:5 | O1010203:22B/ O1010203_U22:6 | [6 empty] | 22A | 22B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03059 | 17XZSL03059 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703003 | DCS_DI_02 | Field |  | 17-C-DD-N-002FL10 | 24 Pair | Pr.16 | 17-MC-DCS-001 | TS-F-06 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1010203_U23 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-P-031A discharge line | 17-XV-03059 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-06:31/ O1010203_U23:3 | TS-F-06:32/ O1010203_U23:4 |  |  | O1010203:23A/ O1010203_U23:5 | O1010203:23B/ O1010203_U23:6 | [6 empty] | 23A | 23B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03059 | 17XY03059 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703003 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.15 | 17-MC-DCS-001 | TS-G-04 | 15 | 16 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 2 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | 17-P-031A discharge line | ЛИНИЯ НАГНЕТАНИЯ P-031A | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:15/ O1010211:2A | TS-G-04:16/ O1010211:2C | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03060 | 17XZSH03060 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703003 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL10 | 12 Pair | Pr.01 | 17-MC-DCS-004 | TS-Q-02 | 1 | 2 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010205_U1 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 1 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | 17-P-031B discharge | 17-XV-03060 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:1/ O1010205_U1:3 | TS-Q-02:2/ O1010205_U1:4 |  |  | O1010205:1A/ O1010205_U1:5 | O1010205:1B/ O1010205_U1:6 | [6 empty] | 1A | 1B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03060 | 17XZSL03060 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703003 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL10 | 12 Pair | Pr.02 | 17-MC-DCS-004 | TS-Q-02 | 3 | 4 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010205_U2 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 2 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | 17-P-031B discharge | 17-XV-03060 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:3/ O1010205_U2:3 | TS-Q-02:4/ O1010205_U2:4 |  |  | O1010205:2A/ O1010205_U2:5 | O1010205:2B/ O1010205_U2:6 | [6 empty] | 2A | 2B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03060 | 17XY03060 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703003 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.17 | 17-MC-DCS-001 | TS-G-04 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 3 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | 17-P-031B discharge | ЛИНИЯ НАГНЕТАНИЯ P-031В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:17/ O1010211:3A | TS-G-04:18/ O1010211:3C | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03061 | 17XZSH03061 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703003 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL10 | 12 Pair | Pr.03 | 17-MC-DCS-004 | TS-Q-02 | 5 | 6 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010205_U3 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 3 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | 17-P-031C discharge | 17-XV-03061 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:5/ O1010205_U3:3 | TS-Q-02:6/ O1010205_U3:4 |  |  | O1010205:3A/ O1010205_U3:5 | O1010205:3B/ O1010205_U3:6 | [6 empty] | 3A | 3B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03061 | 17XZSL03061 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703003 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL10 | 12 Pair | Pr.04 | 17-MC-DCS-004 | TS-Q-02 | 7 | 8 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010205_U4 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 4 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | 17-P-031C discharge | 17-XV-03061 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:7/ O1010205_U4:3 | TS-Q-02:8/ O1010205_U4:4 |  |  | O1010205:4A/ O1010205_U4:5 | O1010205:4B/ O1010205_U4:6 | [6 empty] | 4A | 4B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03061 | 17XY03061 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703003 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.19 | 17-MC-DCS-001 | TS-G-04 | 19 | 20 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 4 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | 17-P-031C discharge | ЛИНИЯ НАГНЕТАНИЯ P-031С | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:19/ O1010211:4A | TS-G-04:20/ O1010211:4C | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03071 | 17XZSH03071 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL10 | 12 Pair | Pr.05 | 17-MC-DCS-004 | TS-Q-02 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010205_U5 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 5 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | Urea Melt Steam Condensate | 17-XV-03071 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:9/ O1010205_U5:3 | TS-Q-02:10/ O1010205_U5:4 |  |  | O1010205:5A/ O1010205_U5:5 | O1010205:5B/ O1010205_U5:6 | [6 empty] | 5A | 5B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03071 | 17XZSL03071 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL10 | 12 Pair | Pr.06 | 17-MC-DCS-004 | TS-Q-02 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010205_U6 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 6 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | Urea Melt Steam Condensate | 17-XV-03071 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:11/ O1010205_U6:3 | TS-Q-02:12/ O1010205_U6:4 |  |  | O1010205:6A/ O1010205_U6:5 | O1010205:6B/ O1010205_U6:6 | [6 empty] | 6A | 6B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03071 | 17XY03071 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703004 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.21 | 17-MC-DCS-001 | TS-G-04 | 21 | 22 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 5 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Urea Melt Steam Condensate | КОНДЕНСАТ ПАРА ПЛАВА КАРБАМИДА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:21/ O1010211:5A | TS-G-04:22/ O1010211:5C | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03072 | 17XZSH03072 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL10 | 12 Pair | Pr.07 | 17-MC-DCS-004 | TS-Q-02 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010205_U7 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 7 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | Urea Melt Steam Condensate | 17-XV-03072 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:13/ O1010205_U7:3 | TS-Q-02:14/ O1010205_U7:4 |  |  | O1010205:7A/ O1010205_U7:5 | O1010205:7B/ O1010205_U7:6 | [6 empty] | 7A | 7B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03072 | 17XZSL03072 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21703004 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL10 | 12 Pair | Pr.08 | 17-MC-DCS-004 | TS-Q-02 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A | O1010205_U8 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 8 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES | Urea Melt Steam Condensate | 17-XV-03072 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-Q-02:15/ O1010205_U8:3 | TS-Q-02:16/ O1010205_U8:4 |  |  | O1010205:8A/ O1010205_U8:5 | O1010205:8B/ O1010205_U8:6 | [6 empty] | 8A | 8B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -03072 | 17XY03072 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21703004 | DCS_DO_01 | Field |  | 17-C-CD-N-002FL10 | 30 Core | C.23 | 17-MC-DCS-001 | TS-G-04 | 23 | 24 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 6 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Urea Melt Steam Condensate | КОНДЕНСАТ ПАРА ПЛАВА КАРБАМИДА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-04:23/ O1010211:6A | TS-G-04:24/ O1010211:6C | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -07021 | 17XZSH07021 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-GF-VD-BD17717L072003 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.09 | 17-MC-DCS-002 | TS-R-03 | 17 | 18 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U1 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | BACKWASH OUTLET FROM FILTER L-72B | 11-XV-07021 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-03:17/ O1011104_U1:3 | TS-R-03:18/ O1011104_U1:4 |  |  | O1011104:1A/ O1011104_U1:5 | O1011104:1B/ O1011104_U1:6 | [6 empty] | 1A | 1B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -07021 | 17XZSL07021 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Close Proximity Switch | 4124-GF-VD-BD17717L072003 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.10 | 17-MC-DCS-002 | TS-R-03 | 19 | 20 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U2 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | BACKWASH OUTLET FROM FILTER L-72B | 11-XV-07021 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-03:19/ O1011104_U2:3 | TS-R-03:20/ O1011104_U2:4 |  |  | O1011104:2A/ O1011104_U2:5 | O1011104:2B/ O1011104_U2:6 | [6 empty] | 2A | 2B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -07021 | 17XY07021 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GF-VD-BD17717L072003 | DCS_DO_01 | Field |  | 17-XY-07021 | 02 Core | C.01 | 17-MC-DCS-007 | TS-F-11 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 18 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | BACKWASH OUTLET FROM FILTER L-72B | ВЫХОД ПРОМЫВКИ ФИЛЬТРА L72B | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-11:1/ O1011210:18A | TS-F-11:2/ O1011210:18C | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -07023 | 17XZSH07023 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-GF-VD-BD17717L072003 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.11 | 17-MC-DCS-002 | TS-R-03 | 21 | 22 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U3 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | BACKWASH OUTLET FROM FILTER L-72A | 11-XV-07023 ОТКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-03:21/ O1011104_U3:3 | TS-R-03:22/ O1011104_U3:4 |  |  | O1011104:3A/ O1011104_U3:5 | O1011104:3B/ O1011104_U3:6 | [6 empty] | 3A | 3B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -07023 | 17XZSL07023 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Close Proximity Switch | 4124-GF-VD-BD17717L072003 | DCS_DI_02 | Field |  | 17-C-DD-N-003FL07 | 24 Pair | Pr.12 | 17-MC-DCS-002 | TS-R-03 | 23 | 24 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011104_U4 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | BACKWASH OUTLET FROM FILTER L-72A | 11-XV-07023 ЗАКРЫТО | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-R-03:23/ O1011104_U4:3 | TS-R-03:24/ O1011104_U4:4 |  |  | O1011104:4A/ O1011104_U4:5 | O1011104:4B/ O1011104_U4:6 | [6 empty] | 4A | 4B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -07023 | 17XY07023 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GF-VD-BD17717L072003 | DCS_DO_01 | Field |  | 17-XY-07023 | 02 Core | C.01 | 17-MC-DCS-007 | TS-F-12 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 19 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | BACKWASH OUTLET FROM FILTER L-72A | ВЫХОД ПРОМЫВКИ ФИЛЬТРА L72А | 17-AMMONIA UTILITIES | 00-Common | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-12:1/ O1011210:19A | TS-F-12:2/ O1011210:19C | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -09005 | 17XZSL09005 |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21709001 | DCS_DI_02 | Field |  | 17-XZSH/L-09005 | 02 Pair | Pr.02 | 17-MC-DCS-009 | TS-G-07 | 3 | 4 |  | 4 | AVK 2,5 A, AVK 2,5 A | O1011115_U1 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | AI From PSA dryer | 17-XV-09005 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-07:3/ O1011115_U1:3 | TS-G-07:4/ O1011115_U1:4 |  |  | O1011115:1A/ O1011115_U1:5 | O1011115:1B/ O1011115_U1:6 | [6 empty] | 1A | 1B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -09005 | 17XZSH09005 |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21709001 | DCS_DI_02 | Field |  | 17-XZSH/L-09005 | 02 Pair | Pr.01 | 17-MC-DCS-009 | TS-G-07 | 1 | 2 |  | 4 | AVK 2,5 A, AVK 2,5 A | O1011115_U13 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | AI From PSA dryer | 17-XV-09005 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-07:1/ O1011115_U13:3 | TS-G-07:2/ O1011115_U13:4 |  |  | O1011115:13A/ O1011115_U13:5 | O1011115:13B/ O1011115_U13:6 | [6 empty] | 13A | 13B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -09005 | 17XY09005 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21709001 | DCS_DO_01 | Field |  | 17-XY-09005 | 02 Core | C.01 | 17-MC-DCS-007 | TS-F-13 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 20 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | AI From PSA dryer | ВОЗДУХ КИП ОТ ОСУШИТЕЛЯ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-13:1/ O1011210:20A | TS-F-13:2/ O1011210:20C | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 | 17XL090301 |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | LP |  | 17-C-DD-N-002-LP003A-L091 | 16 Core | C.01 | 17-MC-DCS-007 | TS-G-03 | 1 | 2 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 13 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | DRYER RUNNING STATUS TRAIN A | ВКЛЮЧЕНИЕ ОСУШКИ ПОТОКА А | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:1/ O1011210:13A | TS-G-03:2/ O1011210:13C | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -A | 17XZSH090301A |  | DI-IS (NAMUR) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.01 | 17-MC-DCS-009 | TS-G-05 | 1 | 2 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U14 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092A | 11-XV-090301-A ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:1/ O1011115_U14:3 | TS-G-05:2/ O1011115_U14:4 |  |  | O1011115:14A/ O1011115_U14:5 | O1011115:14B/ O1011115_U14:6 | [6 empty] | 14A | 14B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -A | 17XZSL090301A |  | DI-IS (NAMUR) DCS |  | Сигнал | Temperature Transmitter - Head Mounted | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.02 | 17-MC-DCS-009 | TS-G-05 | 3 | 4 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U15 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092A | 11-XV-090301-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:3/ O1011115_U15:3 | TS-G-05:4/ O1011115_U15:4 |  |  | O1011115:15A/ O1011115_U15:5 | O1011115:15B/ O1011115_U15:6 | [6 empty] | 15A | 15B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -A | 17XY090301AB |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.01 | 17-MC-DCS-002 | TS-P-02 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 1 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092A | В ОСУШИТЕЛИ 17L091V092A | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:1/ O1011204:1A | TS-P-02:2/ O1011204:1C | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -A | 17XY090301AA |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.03 | 17-MC-DCS-002 | TS-P-02 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 2 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092A | В ОСУШИТЕЛИ 17L091V092A | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:3/ O1011204:2A | TS-P-02:4/ O1011204:2C | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -B | 17XZSH090301B |  | DI-IS (NAMUR) DCS |  | Сигнал | Pressure Transmitter | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.03 | 17-MC-DCS-009 | TS-G-05 | 5 | 6 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U16 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092B | 11-XV-090301-В ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:5/ O1011115_U16:3 | TS-G-05:6/ O1011115_U16:4 |  |  | O1011115:16A/ O1011115_U16:5 | O1011115:16B/ O1011115_U16:6 | [6 empty] | 16A | 16B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -B | 17XZSL090301B |  | DI-IS (NAMUR) DCS |  | Сигнал | Pressure Transmitter | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.04 | 17-MC-DCS-009 | TS-G-05 | 7 | 8 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U17 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092B | 11-XV-090301-В ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:7/ O1011115_U17:3 | TS-G-05:8/ O1011115_U17:4 |  |  | O1011115:17A/ O1011115_U17:5 | O1011115:17B/ O1011115_U17:6 | [6 empty] | 17A | 17B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -B | 17XY090301BB |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.05 | 17-MC-DCS-002 | TS-P-02 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 3 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092B | В ОСУШИТЕЛИ 17L091V092В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:5/ O1011204:3A | TS-P-02:6/ O1011204:3C | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -B | 17XY090301BA |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.07 | 17-MC-DCS-002 | TS-P-02 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 4 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092B | В ОСУШИТЕЛИ 17L091V092В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:7/ O1011204:4A | TS-P-02:8/ O1011204:4C | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -C | 17XZSH090301C |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.13 | 17-MC-DCS-009 | TS-G-05 | 25 | 26 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U5 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092C | 11-XV-090301-С ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:25/ O1011115_U5:3 | TS-G-05:26/ O1011115_U5:4 |  |  | O1011115:5A/ O1011115_U5:5 | O1011115:5B/ O1011115_U5:6 | [6 empty] | 5A | 5B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -C | 17XZSL090301C |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.14 | 17-MC-DCS-009 | TS-G-05 | 27 | 28 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U6 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092C | 11-XV-090301-С ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:27/ O1011115_U6:3 | TS-G-05:28/ O1011115_U6:4 |  |  | O1011115:6A/ O1011115_U6:5 | O1011115:6B/ O1011115_U6:6 | [6 empty] | 6A | 6B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -C | 17XY090301CB |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.17 | 17-MC-DCS-002 | TS-P-02 | 17 | 18 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 7 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092C | В ОСУШИТЕЛИ 17L091V092С | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:17/ O1011204:7A | TS-P-02:18/ O1011204:7C | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -C | 17XY090301CA |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.19 | 17-MC-DCS-002 | TS-P-02 | 19 | 20 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 8 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092C | В ОСУШИТЕЛИ 17L091V092С | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:19/ O1011204:8A | TS-P-02:20/ O1011204:8C | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -D | 17XZSH090301D |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.15 | 17-MC-DCS-009 | TS-G-05 | 29 | 30 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U7 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092D | 11-XV-090301-D ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:29/ O1011115_U7:3 | TS-G-05:30/ O1011115_U7:4 |  |  | O1011115:7A/ O1011115_U7:5 | O1011115:7B/ O1011115_U7:6 | [6 empty] | 7A | 7B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -D | 17XZSL090301D |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.16 | 17-MC-DCS-009 | TS-G-05 | 31 | 32 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U8 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092D | 11-XV-090301-D ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:31/ O1011115_U8:3 | TS-G-05:32/ O1011115_U8:4 |  |  | O1011115:8A/ O1011115_U8:5 | O1011115:8B/ O1011115_U8:6 | [6 empty] | 8A | 8B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -D | 17XY090301DB |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.21 | 17-MC-DCS-002 | TS-P-02 | 21 | 22 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 9 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092D | В ОСУШИТЕЛИ 17L091V092D | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:21/ O1011204:9A | TS-P-02:22/ O1011204:9C | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090301 -D | 17XY090301DA |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.23 | 17-MC-DCS-002 | TS-P-02 | 23 | 24 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 10 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To DECISSANT TOWER 17-L-091-V-092D | В ОСУШИТЕЛИ 17L091V092D | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:23/ O1011204:10A | TS-P-02:24/ O1011204:10C | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 | 17XL090302 |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | LP |  | 17-C-DD-N-002-LP003A-L091 | 16 Core | C.03 | 17-MC-DCS-007 | TS-G-03 | 3 | 4 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 14 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | DRYER ALARM STATUS TRAIN A | АВАРИЯ ОСУШКИ ПОТОКА А | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:3/ O1011210:14A | TS-G-03:4/ O1011210:14C | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -A | 17XZSH090302A |  | DI-IS (NAMUR) DCS |  | Сигнал | Pressure Transmitter | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.05 | 17-MC-DCS-009 | TS-G-05 | 9 | 10 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U18 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | 11-XV-090302-A ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:9/ O1011115_U18:3 | TS-G-05:10/ O1011115_U18:4 |  |  | O1011115:18A/ O1011115_U18:5 | O1011115:18B/ O1011115_U18:6 | [6 empty] | 18A | 18B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -A | 17XZSL090302A |  | DI-IS (NAMUR) DCS |  | Сигнал | DP Flow Transmitter | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.06 | 17-MC-DCS-009 | TS-G-05 | 11 | 12 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U19 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | 11-XV-090302-A ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:11/ O1011115_U19:3 | TS-G-05:12/ O1011115_U19:4 |  |  | O1011115:19A/ O1011115_U19:5 | O1011115:19B/ O1011115_U19:6 | [6 empty] | 19A | 19B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -A | 17XY090302A |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.09 | 17-MC-DCS-002 | TS-P-02 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 5 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | В БЕЗОПАСНОЕ МЕСТО АТМОСФЕРУ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:9/ O1011204:5A | TS-P-02:10/ O1011204:5C | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -B | 17XZSH090302B |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.07 | 17-MC-DCS-009 | TS-G-05 | 13 | 14 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U3 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | 11-XV-090302-B ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:13/ O1011115_U3:3 | TS-G-05:14/ O1011115_U3:4 |  |  | O1011115:3A/ O1011115_U3:5 | O1011115:3B/ O1011115_U3:6 | [6 empty] | 3A | 3B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -B | 17XZSL090302B |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.08 | 17-MC-DCS-009 | TS-G-05 | 15 | 16 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U4 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | 11-XV-090302-B ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:15/ O1011115_U4:3 | TS-G-05:16/ O1011115_U4:4 |  |  | O1011115:4A/ O1011115_U4:5 | O1011115:4B/ O1011115_U4:6 | [6 empty] | 4A | 4B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -B | 17XY090302B |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.11 | 17-MC-DCS-002 | TS-P-02 | 11 | 12 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 6 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | В БЕЗОПАСНОЕ МЕСТО АТМОСФЕРУ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:11/ O1011204:6A | TS-P-02:12/ O1011204:6C | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -C | 17XZSH090302C |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.17 | 17-MC-DCS-009 | TS-G-05 | 33 | 34 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U9 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | 11-XV-090302-C ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:33/ O1011115_U9:3 | TS-G-05:34/ O1011115_U9:4 |  |  | O1011115:9A/ O1011115_U9:5 | O1011115:9B/ O1011115_U9:6 | [6 empty] | 9A | 9B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -C | 17XZSL090302C |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.18 | 17-MC-DCS-009 | TS-G-05 | 35 | 36 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U10 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | 11-XV-090302-C ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:35/ O1011115_U10:3 | TS-G-05:36/ O1011115_U10:4 |  |  | O1011115:10A/ O1011115_U10:5 | O1011115:10B/ O1011115_U10:6 | [6 empty] | 10A | 10B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -C | 17XY090302C |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.25 | 17-MC-DCS-002 | TS-P-02 | 25 | 26 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 11 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | В БЕЗОПАСНОЕ МЕСТО АТМОСФЕРУ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:25/ O1011204:11A | TS-P-02:26/ O1011204:11C | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -D | 17XZSH090302D |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.19 | 17-MC-DCS-009 | TS-G-05 | 37 | 38 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U11 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | 11-XV-090302-D ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:37/ O1011115_U11:3 | TS-G-05:38/ O1011115_U11:4 |  |  | O1011115:11A/ O1011115_U11:5 | O1011115:11B/ O1011115_U11:6 | [6 empty] | 11A | 11B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -D | 17XZSL090302D |  | DI-IS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DI_02 | Field |  | 17-C-DD-I-005FL10-L091 | 24 Pair | Pr.20 | 17-MC-DCS-009 | TS-G-05 | 39 | 40 |  | 48 | AVK 2,5 A, AVK 2,5 A | O1011115_U12 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | 11-XV-090302-D ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-G-05:39/ O1011115_U12:3 | TS-G-05:40/ O1011115_U12:4 |  |  | O1011115:12A/ O1011115_U12:5 | O1011115:12B/ O1011115_U12:6 | [6 empty] | 12A | 12B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090302 -D | 17XY090302D |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | Field |  | 17-C-CD-N-006FL10-L091 | 30 Core | C.27 | 17-MC-DCS-002 | TS-P-02 | 27 | 28 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 12 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | To ATM Safe location | В БЕЗОПАСНОЕ МЕСТО АТМОСФЕРУ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-P-02:27/ O1011204:12A | TS-P-02:28/ O1011204:12C | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090351 | 17XL090351 |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | LP |  | 17-C-DD-N-002-LP003B-L091 | 02 Core | C.01 | 17-MC-DCS-007 | TS-H-01 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 16 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | DRYER RUNNING STATUS TRAIN B | ВКЛЮЧЕНИЕ ОСУШКИ ПОТОКА В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-01:1/ O1011210:16A | TS-H-01:2/ O1011210:16C | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -090352 | 17XL090352 |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GY-VD-BD17517L091091_SH.2 | DCS_DO_01 | LP |  | 17-C-DD-N-002-LP003A-L091 | 16 Core | C.11 | 17-MC-DCS-007 | TS-G-03 | 11 | 12 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 15 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | DRYER ALARM STATUS TRAIN B | АВАРИЯ ОСУШКИ ПОТОКА В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants |  | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-03:11/ O1011210:15A | TS-G-03:12/ O1011210:15C | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -100245 | 17XA100245AY |  | DI-NIS (VFC) DCS |  | Сигнал | Exchange Signal | 4124-FY-VD-BD17517L10100002 | DCS_DI_01 | RR-AM |  | 17-I-DD-N-002-BL02-L101 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-H-04 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Nitrogen Package OSS Train A activation Alarm | ПОДАЧА АЗОТА ТРЕНИРОВКА А | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC-S | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-04:5/ O1011113:21A | TS-H-04:6/ O1011113:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -10060 | 17XZSH10060 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21710001 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL10 | 06 Pair | Pr.01 | 17-MC-DCS-001 | TS-F-03 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010203_U2 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | 17-XV-10060 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-03:1/ O1010203_U2:3 | TS-F-03:2/ O1010203_U2:4 |  |  | O1010203:2A/ O1010203_U2:5 | O1010203:2B/ O1010203_U2:6 | [6 empty] | 2A | 2B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -10060 | 17XZSL10060 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21710001 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL10 | 06 Pair | Pr.02 | 17-MC-DCS-001 | TS-F-03 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010203_U3 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | 17-XV-10060 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-03:3/ O1010203_U3:3 | TS-F-03:4/ O1010203_U3:4 |  |  | O1010203:3A/ O1010203_U3:5 | O1010203:3B/ O1010203_U3:6 | [6 empty] | 3A | 3B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -10060 | 17XY10060 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21710001 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL10 | 16 Core | C.01 | 17-MC-DCS-001 | TS-G-02 | 1 | 2 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 13 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | АЗОТ ИЗ V-106 СЕТЬ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:1/ O1010210:13A | TS-G-02:2/ O1010210:13C | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -10061 | 17XZSH10061 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21710001 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL10 | 06 Pair | Pr.03 | 17-MC-DCS-001 | TS-F-03 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010203_U4 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | 17-XV-10061 ОТКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-03:5/ O1010203_U4:3 | TS-F-03:6/ O1010203_U4:4 |  |  | O1010203:4A/ O1010203_U4:5 | O1010203:4B/ O1010203_U4:6 | [6 empty] | 4A | 4B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -10061 | 17XZSL10061 |  | DI-NIS (NAMUR) DCS |  | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21710001 | DCS_DI_02 | Field |  | 17-C-DD-N-001FL10 | 06 Pair | Pr.04 | 17-MC-DCS-001 | TS-F-03 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A | O1010203_U5 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | 17-XV-10061 ЗАКРЫТО | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-F-03:7/ O1010203_U5:3 | TS-F-03:8/ O1010203_U5:4 |  |  | O1010203:5A/ O1010203_U5:5 | O1010203:5B/ O1010203_U5:6 | [6 empty] | 5A | 5B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -10061 | 17XY10061 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21710001 | DCS_DO_01 | Field |  | 17-C-CD-N-001FL10 | 16 Core | C.03 | 17-MC-DCS-001 | TS-G-02 | 3 | 4 |  | 16 | AVK 2,5 A, AVK 2,5 A |  |  | O1010210 | TUA711-DOR32 | 17-SC-DCS-001/O1010210/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010210 | 11 | 14 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | From 17-V-106 to N2 network | АЗОТ ИЗ V-106 СЕТЬ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | CLOSE | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:3/ O1010210:14A | TS-G-02:4/ O1010210:14C | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -100700 | 17XL100700 |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_01 | LP |  | 17-C-DD-002-LP001-K101 | 30 Core | C.01 | 17-MC-DCS-007 | TS-G-01 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 1 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | SEQUENCE READY TO START | ГОТОВНОСТЬ К ПУСКУ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-G-01:1/ O1011210:1A | TS-G-01:2/ O1011210:1C | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -100701 | 17XL100701 |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_01 | LP |  | 17-C-DD-002-LP001-K101 | 30 Core | C.03 | 17-MC-DCS-007 | TS-G-01 | 3 | 4 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 2 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | OIL PUMP RUNNING | МАСЛЯНЫЙ НАСОС РАБОТАЕТ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-G-01:3/ O1011210:2A | TS-G-01:4/ O1011210:2C | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -100702 | 17XL100702 |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_01 | LP |  | 17-C-DD-002-LP001-K101 | 30 Core | C.05 | 17-MC-DCS-007 | TS-G-01 | 5 | 6 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 3 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | COMPRESSOR RUNNING | КОМПРЕССОР РАБОТАЕТ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-G-01:5/ O1011210:3A | TS-G-01:6/ O1011210:3C | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -100703 | 17XL100703 |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_01 | LP |  | 17-C-DD-002-LP001-K101 | 30 Core | C.07 | 17-MC-DCS-007 | TS-G-01 | 7 | 8 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 4 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | COMMON ALARM | ОБЩАЯ СИГНАЛИЗАЦИЯ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-G-01:7/ O1011210:4A | TS-G-01:8/ O1011210:4C | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -100704 | 17XL100704 |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DO_01 | LP |  | 17-C-DD-002-LP001-K101 | 30 Core | C.09 | 17-MC-DCS-007 | TS-G-01 | 9 | 10 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 5 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | COMMON SHUTDOWN | ОБЩИЙ ОСТАНОВ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-G-01:9/ O1011210:5A | TS-G-01:10/ O1011210:5C | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -11250 -A | 17XL11250A |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GG-VD-BD17117P111037_SH.2 | DCS_DO_01 | LP |  | 17-C-DD-N-002-LP001-P111A | 02 Core | C.01 | 17-MC-DCS-007 | TS-H-02 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 9 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Ready to Start Lamp | ГОТОВНОСТЬ К ЗАПУСКУ ЛАМПА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-02:1/ O1011210:9A | TS-H-02:2/ O1011210:9C | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -11250 -B | 17XA11250B |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-GG-VD-BD17117P111037_SH.2 | DCS_DO_01 | LP |  | 17-C-DD-N-003-LP001-P111A | 02 Core | C.01 | 17-MC-DCS-007 | TS-H-03 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 17 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | Common Alarm Lamp | ОБЩАЯ АВАРИЯ ЛАМПА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-03:1/ O1011210:17A | TS-H-03:2/ O1011210:17C | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.12 |  | Резерв |  | DI-NIS (VFC) DCS | 08.04.25 сигнал 17XA11281X исключен по TQ-132 | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 9 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-F-05 клеммы 1, 2 до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113637 | 17XS113637 |  | DI-NIS (VFC) DCS |  | Сигнал | Status Contact | 4124-FB-VD-BD00317L11111388 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003-L111 | 12 Pair | Pr.08 | 17-MC-DCS-001 | TS-F-04 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From Strainer 17-L-111-S-140 | Из фильтра 17-L-111-S-140 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:15/ O1010200:24A | TS-F-04:16/ O1010200:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113638 | 17XS113638 |  | DI-NIS (VFC) DCS |  | Сигнал | Status Contact | 4124-FB-VD-BD00317L11111388 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003-L111 | 12 Pair | Pr.09 | 17-MC-DCS-001 | TS-F-04 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From Strainer 17-L-111-S-141 | Из фильтра 17-L-111-S-141 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:17/ O1010200:25A | TS-F-04:18/ O1010200:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113639 | 17XS113639 |  | DI-NIS (VFC) DCS |  | Сигнал | Status Contact | 4124-FB-VD-BD00317L11111388 | DCS_DI_01 | LP |  | 17-C-DD-N-001-LP003-L111 | 12 Pair | Pr.10 | 17-MC-DCS-001 | TS-F-04 | 19 | 20 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | From Strainer 17-L-111-S-142 | Из фильтра 17-L-111-S-142 | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-04:19/ O1010200:26A | TS-F-04:20/ O1010200:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113800 | 17XA113800X |  | DI-NIS (VFC) DCS |  | Сигнал | Lamp | 4124-FB-VD-BD00317L11111372_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-008BL02 | 12 Pair | Pr.08 | 17-MC-DCS-007 | TS-F-10 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 19 | DI715-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | BOILER TRIP | ПОДАЧА ТОПЛИВА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | BMS | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-10:15/ O1011113:19A | TS-F-10:16/ O1011113:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113803 | 17XA113803X |  | DI-NIS (VFC) DCS |  | Сигнал | Lamp | 4124-FB-VD-BD00317L11111372_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-008BL02 | 12 Pair | Pr.09 | 17-MC-DCS-007 | TS-F-10 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 20 | DI715-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | NATURAL DRAFT REQUESTED | ЗАПРОС ??? | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | BMS | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-10:17/ O1011113:20A | TS-F-10:18/ O1011113:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113804 | 17XA113804X |  | DI-NIS (VFC) DCS |  | Сигнал | Lamp | 4124-FB-VD-BD00317L11111372_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-008BL02 | 12 Pair | Pr.06 | 17-MC-DCS-007 | TS-F-10 | 11 | 12 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 17 | DI715-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | WAITING TIME FOR AIR TRIP | ВРЕМЯ ОЖИДАНИЯ ПОДАЧИ ВОЗДУХА | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | BMS | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-10:11/ O1011113:17A | TS-F-10:12/ O1011113:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113809 | 17XA113809X |  | DI-NIS (VFC) DCS |  | Сигнал | Lamp | 4124-FB-VD-BD00317L11111372_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-008BL02 | 12 Pair | Pr.07 | 17-MC-DCS-007 | TS-F-10 | 13 | 14 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 18 | DI715-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | POST PURGE FAILURE | СБОЙ ПОСЛЕ ПРОДУВКИ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | BMS | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-10:13/ O1011113:18A | TS-F-10:14/ O1011113:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113857 | 17XA113857X |  | DI-NIS (VFC) DCS |  | Сигнал | Lamp | 4124-FB-VD-BD00317L11111372_SH.3 | DCS_DI_01 | RR-AM |  | 17-I-DE-N-008BL02 | 12 Pair | Pr.05 | 17-MC-DCS-007 | TS-F-10 | 9 | 10 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 16 | DI715-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | ONE PILOT BURNER ON | ОДНА ПИЛОТНАЯ ГОРЕЛКА ВКЛ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | BMS | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-10:9/ O1011113:16A | TS-F-10:10/ O1011113:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113930 -A | 17XL113930A |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-FB-VD-BD00317L11111310 | DCS_DO_01 | LP |  | 17-C-DD-N-002-LP002-L111 | 08 Core | C.01 | 17-MC-DCS-007 | TS-G-02 | 1 | 2 |  | 8 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE READY TO START | ПАР ТУРБИНА ГОТОВА К ЗАПУСКУ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:1/ O1011210:10A | TS-G-02:2/ O1011210:10C | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113931 -A | 17XL113931A |  | DO-NIS (24VDC) DCS |  | Сигнал | ALARM | 4124-FB-VD-BD00317L11111310 | DCS_DO_01 | LP |  | 17-C-DD-N-002-LP002-L111 | 08 Core | C.03 | 17-MC-DCS-007 | TS-G-02 | 3 | 4 |  | 8 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 11 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE ALARM | АВАРИЯ ПАРОВОЙ ТУРБИНЫ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | LAMP ON | LAMP OFF | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:3/ O1011210:11A | TS-G-02:4/ O1011210:11C | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113933-A | 17XL113933A |  | DO-NIS (24VDC) DCS |  | Сигнал | Lamp | 4124-FB-VD-BD00317L11111310 | DCS_DO_01 | Field |  | 17-C-DD-N-002-LP002-L111 | 08 Core | C.05 | 17-MC-DCS-007 | TS-G-02 | 5 | 6 |  | 8 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 12 | DO716-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | STEAM TURBINE ALARM | АВАРИЙНЫЙ СИГНАЛ ПАРОВОЙ ТУРБИНЫ | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-G-02:5/ O1011210:12A | TS-G-02:6/ O1011210:12C | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -113938 -X | 17XA113938X |  | DI-NIS (VFC) DCS |  | Сигнал | Alarm | 4124-FB-VD-BD00317L11111310 | DCS_DI_01 | RR-AM |  | 17-I-DD-N-023BL02 | 02 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-05 | 3 | 4 |  | 4 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 10 | DI715-S11 | 32 | 0.1 |  |  | DCS AMMONIA-UTILITIES | 17-L-111-STK-101-A OST Common Alarm | АВАРИЯ ПУСКА 17-L-111-STK-101-A | 17-AMMONIA UTILITIES | 11-Auxiliary Boiler Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | OST | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-05:3/ O1011113:10A | TS-F-05:4/ O1011113:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.3 | 17-X -17101 | 17XZSH17101 |  | DI-NIS (NAMUR) DCS | изм номер клеммной группы (TQ_074) | Сигнал | Position Open Proximity Switch | 4124-XZ-DM-21717101 | DCS_DI_02 | Field |  | 17-XZSH/L-17101 | 02 Pair | Pr.01 | 17-MC-DCS-002 | TS-P-09 | 1 | 2 |  | 4 | AVK 2,5 A, AVK 2,5 A | O1011104_U26 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Glycol water return service | 17-XV-17101 ОТКРЫТО | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | OPEN | NOT OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-09:1/ O1011104_U26:3 | TS-P-09:2/ O1011104_U26:4 |  |  | O1011104:26A/ O1011104_U26:5 | O1011104:26B/ O1011104_U26:6 | [6 empty] | 26A | 26B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.3 | 17-X -17101 | 17XZSL17101 |  | DI-NIS (NAMUR) DCS | изм номер клеммной группы (TQ_074) | Сигнал | Position Closed Proximity Switch | 4124-XZ-DM-21717101 | DCS_DI_02 | Field |  | 17-XZSH/L-17101 | 02 Pair | Pr.02 | 17-MC-DCS-002 | TS-P-09 | 3 | 4 |  | 4 | AVK 2,5 A, AVK 2,5 A | O1011104_U27 | HD5516 | O1011104 | TUA711-DIO32 | 17-SC-DCS-002/O1011104/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011104 | 5 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Glycol water return service | 17-XV-17101 ЗАКРЫТО | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSED | NOT CLOSED | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [12 empty] | TS-P-09:3/ O1011104_U27:3 | TS-P-09:4/ O1011104_U27:4 |  |  | O1011104:27A/ O1011104_U27:5 | O1011104:27B/ O1011104_U27:6 | [6 empty] | 27A | 27B | 3 | 4 |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -17101 | 17XY17101 |  | DO-NIS (24VDC) DCS |  | Сигнал | Solenoid Valve | 4124-XZ-DM-21717101 | DCS_DO_01 | Field |  | 17-XY-17101 | 02 Core | C.01 | 17-MC-DCS-007 | TS-F-14 | 1 | 2 |  | 2 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 21 | DO716-S11 | 32 | 0.25 |  |  | DCS AMMONIA-UTILITIES | Glycol water return service | ВОЗВРАТ ВОДНО-ГЛИКОЛЕВОЙ СМЕСИ | 17-AMMONIA UTILITIES | 17-Glycol Preparation Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- | CLOSE | OPEN | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-14:1/ O1011210:21A | TS-F-14:2/ O1011210:21C | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X -99999 | 17XS99999Y |  | DO-NIS (VFC NO) DCS |  | Сигнал | Exchange Signal | 4124-FY-VD-BD17517L10100002 | DCS_DO_02 | RR-AM |  | 17-I-DD-N-001-BL02-L101 | 30 Core | C.01 | 17-MC-DCS-007 | TS-H-07 | 1 | 2 |  | 30 | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Time synchronization command For Nitrogen Unit PLC | СИНХР ВРЕМ ПЛК АЗОТ УСТАНОВКИ | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC-C | SYNC | NO ACTION | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-07:1/ O1011211:11A | TS-H-07:2/ O1011211:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X-100245 | 17XA100245BY |  | DI-NIS (VFC) DCS |  | Сигнал | Exchange Signal | 4124-FY-VD-BD17517L10100002 | DCS_DI_01 | RR-AM |  | 17-I-DD-N-002-BL02-L101 | 06 Pair | Pr.04 | 17-MC-DCS-007 | TS-H-04 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | Nitrogen Package OSS Train B activation Alarm | ПОДАЧА АЗОТА ТРЕНИРОВКА В | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | PLC-S | ALARM | NORMAL | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-H-04:7/ O1011113:22A | TS-H-04:8/ O1011113:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-X-113950 | 17XA113950 |  | DO-NIS (24VDC) DCS |  | Сигнал | 0 |  | DCS_DO_01 | Field |  | 17-C-DD-N-001-LP002-L111 | 12 Pair | Pr.09 | 17-MC-DCS-007 | TS-F-02 | 17 | 18 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17XA113950 | 17XA113950 | 17-AMMONIA UTILITIES | 07-Cooling Tower Area | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-02:17/ O1011210:8A | TS-F-02:18/ O1011210:8C | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1001 | 17XAD1001 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-101BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-05 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-DCS-001 HIGH TEMPERATURE | 17-SC-DCS-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-05:1/ O1011200:1A | TS-G-05:2/ O1011200:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1002 | 17XAD1002 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-101BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-05 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-DCS-001 POWER FAIL | 17-SC-DCS-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-05:3/ O1011200:2A | TS-G-05:4/ O1011200:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1003 | 17XAD1003 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-101BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-05 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-DCS-001 FAN FAILURE | 17-SC-DCS-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-05:5/ O1011200:3A | TS-G-05:6/ O1011200:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1004 | 17XAD1004 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-101BL02 | 06 Pair | Pr.04 | 17-MC-DCS-007 | TS-G-05 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-DCS-001 SWITCH FAILURE | 17-SC-DCS-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-05:7/ O1011200:4A | TS-G-05:8/ O1011200:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1005 | 17XAD1005 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-102BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-06 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-DCS-002 HIGH TEMPERATURE | 17-SC-DCS-002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-06:1/ O1011200:5A | TS-G-06:2/ O1011200:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1006 | 17XAD1006 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-102BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-06 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-DCS-002 POWER FAIL | 17-SC-DCS-002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-06:3/ O1011200:6A | TS-G-06:4/ O1011200:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1007 | 17XAD1007 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-102BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-06 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-DCS-002 FAN FAILURE | 17-SC-DCS-002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-06:5/ O1011200:7A | TS-G-06:6/ O1011200:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1008 | 17XAD1008 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-103BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-07 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-001/002 POWER FAIL | 17-MC-DCS-001/002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-07:3/ O1011200:9A | TS-G-07:4/ O1011200:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1009 | 17XAD1009 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-103BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-07 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-001/002 HIGH TEMPERATURE | 17-MC-DCS-001/002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-07:1/ O1011200:8A | TS-G-07:2/ O1011200:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1010 | 17XAD1010 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-103BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-07 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-001/002 FAN FAILURE | 17-MC-DCS-001/002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-07:5/ O1011200:10A | TS-G-07:6/ O1011200:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1011 | 17XAD1011 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-104BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-08 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-003/004 HIGH TEMPERATURE | 17-MC-DCS-003/004 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-08:1/ O1011200:11A | TS-G-08:2/ O1011200:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1012 | 17XAD1012 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-104BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-08 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-003/004 POWER FAIL | 17-MC-DCS-003/004 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-08:3/ O1011200:12A | TS-G-08:4/ O1011200:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1013 | 17XAD1013 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-104BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-08 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-003/004 FAN FAILURE | 17-MC-DCS-003/004 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-08:5/ O1011200:13A | TS-G-08:6/ O1011200:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1014 | 17XAD1014 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-105BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-09 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-005/006 HIGH TEMPERATURE | 17-MC-DCS-005/006 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09:1/ O1011200:14A | TS-G-09:2/ O1011200:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1015 | 17XAD1015 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-105BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-09 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-005/006 POWER FAIL | 17-MC-DCS-005/006 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09:3/ O1011200:15A | TS-G-09:4/ O1011200:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1016 | 17XAD1016 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-105BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-09 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-005/006 FAN FAILURE | 17-MC-DCS-005/006 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-09:5/ O1011200:16A | TS-G-09:6/ O1011200:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1017 | 17XAD1017 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-106BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-10 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-007/008 HIGH TEMPERATURE | 17-MC-DCS-007/008 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-10:1/ O1011200:17A | TS-G-10:2/ O1011200:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1018 | 17XAD1018 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-106BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-10 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-007/008 POWER FAIL | 17-MC-DCS-007/008 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-10:3/ O1011200:18A | TS-G-10:4/ O1011200:18B | [10 empty] | 18A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1019 | 17XAD1019 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-106BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-10 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-007/008 FAN FAILURE | 17-MC-DCS-007/008 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-10:5/ O1011200:19A | TS-G-10:6/ O1011200:19B | [10 empty] | 19A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1020 | 17XAD1020 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-107BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-11 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-009 HIGH TEMPERATURE | 17-MC-DCS-009 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-11:1/ O1011200:20A | TS-G-11:2/ O1011200:20B | [10 empty] | 20A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1021 | 17XAD1021 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-107BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-11 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-009 POWER FAIL | 17-MC-DCS-009 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-11:3/ O1011200:21A | TS-G-11:4/ O1011200:21B | [10 empty] | 21A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1022 | 17XAD1022 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-107BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-11 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-DCS-009 FAN FAILURE | 17-MC-DCS-009 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-11:5/ O1011200:22A | TS-G-11:6/ O1011200:22B | [10 empty] | 22A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1023 | 17XAD1023 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-108BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-12 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-ESD-001 HIGH TEMPERATURE | 17-SC-ESD-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-12:1/ O1011200:23A | TS-G-12:2/ O1011200:23B | [10 empty] | 23A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1024 | 17XAD1024 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-108BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-12 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-ESD-001 POWER FAIL | 17-SC-ESD-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-12:3/ O1011200:24A | TS-G-12:4/ O1011200:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1025 | 17XAD1025 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-108BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-12 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-ESD-001 FAN FAILURE | 17-SC-ESD-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-12:5/ O1011200:25A | TS-G-12:6/ O1011200:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1026 | 17XAD1026 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-109BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-13 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-ESD-002 HIGH TEMPERATURE | 17-SC-ESD-002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-13:1/ O1011200:26A | TS-G-13:2/ O1011200:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1027 | 17XAD1027 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-109BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-13 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-ESD-002 POWER FAIL | 17-SC-ESD-002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-13:3/ O1011200:27A | TS-G-13:4/ O1011200:27B | [10 empty] | 27A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1028 | 17XAD1028 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-109BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-13 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-ESD-002 FAN FAILURE | 17-SC-ESD-002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-13:5/ O1011200:28A | TS-G-13:6/ O1011200:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1029 | 17XAD1029 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-117BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-18 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-ESD-003 HIGH TEMPERATURE | 17-SC-ESD-003 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-18:1/ O1011200:29A | TS-G-18:2/ O1011200:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1030 | 17XAD1030 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-117BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-18 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-ESD-003 POWER FAIL | 17-SC-ESD-003 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-18:3/ O1011200:30A | TS-G-18:4/ O1011200:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1031 | 17XAD1031 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-117BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-18 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-ESD-003 FAN FAILURE | 17-SC-ESD-003 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-18:5/ O1011200:31A | TS-G-18:6/ O1011200:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.7 | 17-X-D1032 | 17XAD1032 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 11.03.2024 изм.TAG_SERVICE | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-110BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-14 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-001 HIGH TEMPERATURE | 17-MC-ESD-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-14:1/ O1011201:1A | TS-G-14:2/ O1011201:1B | [10 empty] | 1A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.7 | 17-X-D1033 | 17XAD1033 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 11.03.2024 изм.TAG_SERVICE | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-110BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-14 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-001 POWER FAIL | 17-MC-ESD-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-14:3/ O1011201:2A | TS-G-14:4/ O1011201:2B | [10 empty] | 2A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.7 | 17-X-D1034 | 17XAD1034 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 11.03.2024 изм.TAG_SERVICE | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-110BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-14 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-001 FAN FAILURE | 17-MC-ESD-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-14:5/ O1011201:3A | TS-G-14:6/ O1011201:3B | [10 empty] | 3A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.7 | 17-X-D1035 | 17XAD1035 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 11.03.2024 изм.TAG_SERVICE | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-111BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-15 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-002/003 HIGH TEMPERATURE | 17-MC-ESD-002/003 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-15:1/ O1011201:4A | TS-G-15:2/ O1011201:4B | [10 empty] | 4A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.7 | 17-X-D1036 | 17XAD1036 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 11.03.2024 изм.TAG_SERVICE | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-111BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-15 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-002/003 POWER FAIL | 17-MC-ESD-002/003 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-15:3/ O1011201:5A | TS-G-15:4/ O1011201:5B | [10 empty] | 5A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.7 | 17-X-D1037 | 17XAD1037 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 11.03.2024 изм.TAG_SERVICE | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-111BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-15 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-002/003 FAN FAILURE | 17-MC-ESD-002/003 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-15:5/ O1011201:6A | TS-G-15:6/ O1011201:6B | [10 empty] | 6A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.7 | 17-X-D1038 | 17XAD1038 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 11.03.2024 изм.TAG_SERVICE | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-112BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-16 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-004/005 HIGH TEMPERATURE | 17-MC-ESD-004/005 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-16:1/ O1011201:7A | TS-G-16:2/ O1011201:7B | [10 empty] | 7A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.7 | 17-X-D1039 | 17XAD1039 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 11.03.2024 изм.TAG_SERVICE | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-112BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-16 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-004/005 POWER FAIL | 17-MC-ESD-004/005 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-16:3/ O1011201:8A | TS-G-16:4/ O1011201:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.7 | 17-X-D1040 | 17XAD1040 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 11.03.2024 изм.TAG_SERVICE | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-112BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-16 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-004/005 FAN FAILURE | 17-MC-ESD-004/005 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-16:5/ O1011201:9A | TS-G-16:6/ O1011201:9B | [10 empty] | 9A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1041 | 17XAD1041 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-118BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-19 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-006/007 HIGH TEMPERATURE | 17-MC-ESD-006/007 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-19:1/ O1011201:24A | TS-G-19:2/ O1011201:24B | [10 empty] | 24A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1042 | 17XAD1042 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-118BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-19 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-006/007 POWER FAIL | 17-MC-ESD-006/007 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-19:3/ O1011201:25A | TS-G-19:4/ O1011201:25B | [10 empty] | 25A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1043 | 17XAD1043 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-118BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-19 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-006/007 FAN FAILURE | 17-MC-ESD-006/007 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-19:5/ O1011201:26A | TS-G-19:6/ O1011201:26B | [10 empty] | 26A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1044 | 17XAD1044 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 12.07.2024 добавлен сигнал диагностики | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-119BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-19 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-008 HIGH TEMPERATURE | 17-MC-ESD-008 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-19:1/ O1011114:28A | TS-F-19:2/ O1011114:28B | [10 empty] | 28A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1045 | 17XAD1045 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 12.07.2024 добавлен сигнал диагностики | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-119BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-19 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-008 POWER FAIL | 17-MC-ESD-008 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-19:3/ O1011114:29A | TS-F-19:4/ O1011114:29B | [10 empty] | 29A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1046 | 17XAD1046 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег 12.07.2024 добавлен сигнал диагностики | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-119BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-F-19 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-MC-ESD-008 FAN FAILURE | 17-MC-ESD-008 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-19:5/ O1011114:30A | TS-F-19:6/ O1011114:30B | [10 empty] | 30A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1047 | 17XAD1047 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-113BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-G-17 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-CP-IRP-001/002/003/004 HIGH TEMPERATURE | 17-CP-IRP-001/002/003/004 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-17:1/ O1011201:10A | TS-G-17:2/ O1011201:10B | [10 empty] | 10A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1048 | 17XAD1048 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-113BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-G-17 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-CP-IRP-001/002/003/004 POWER FAIL | 17-CP-IRP-001/002/003/004 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-17:3/ O1011201:11A | TS-G-17:4/ O1011201:11B | [10 empty] | 11A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1049 | 17XAD1049 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-113BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-G-17 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-CP-IRP-001/002/003/004 FAN FAILURE | 17-CP-IRP-001/002/003/004 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-17:5/ O1011201:12A | TS-G-17:6/ O1011201:12B | [10 empty] | 12A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1050 | 17XAD1050 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-114BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-06 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-CP-AUX-001 HIGH TEMPERATURE | 17-CP-AUX-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-06:1/ O1011201:13A | TS-F-06:2/ O1011201:13B | [10 empty] | 13A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1051 | 17XAD1051 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-114BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-06 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-CP-AUX-001 POWER FAIL | 17-CP-AUX-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-06:3/ O1011201:14A | TS-F-06:4/ O1011201:14B | [10 empty] | 14A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1052 | 17XAD1052 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-114BL02 | 06 Pair | Pr.03 | 17-MC-DCS-007 | TS-F-06 | 5 | 6 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-CP-AUX-001 FAN FAILURE | 17-CP-AUX-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-06:5/ O1011201:15A | TS-F-06:6/ O1011201:15B | [10 empty] | 15A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1053 | 17XAD1053 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-115BL02 | 06 Pair | Pr.01 | 17-MC-DCS-007 | TS-F-07 | 1 | 2 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-CP-MMS-001 HIGH TEMPERATURE | 17-CP-MMS-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-07:1/ O1011201:16A | TS-F-07:2/ O1011201:16B | [10 empty] | 16A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.2 | 17-X-D1054 | 17XAD1054 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 изм тег | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-115BL02 | 06 Pair | Pr.02 | 17-MC-DCS-007 | TS-F-07 | 3 | 4 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-CP-MMS-001 POWER FAIL | 17-CP-MMS-001 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-F-07:3/ O1011201:17A | TS-F-07:4/ O1011201:17B | [10 empty] | 17A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.9 |  | Резерв |  | DI-NIS (Diagnostic) DCS | 31.03.25 сигнал 17XAD1055 удален по TQ-126 25.07.2024 изм тег | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 18 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-F-07 клеммы 5, 6 до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.9 |  | Резерв |  | DI-NIS (Diagnostic) DCS | 31.03.25 сигнал 17XAD1056 удален по TQ-126 25.07.2024 изм тег | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 19 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-F-07 клеммы 7, 8 до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.9 |  | Резерв |  | DI-NIS (Diagnostic) DCS | 31.03.25 сигнал 17XAD1057 удален по TQ-126 25.07.2024 изм тег | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 20 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-F-08 клеммы 1, 2 до терм платы удалить маркировку клеммной группы TS-F-08 | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.9 |  | Резерв |  | DI-NIS (Diagnostic) DCS | 31.03.25 сигнал 17XAD1058 удален по TQ-126 25.07.2024 изм тег | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 21 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-F-08 клеммы 3, 4 до терм платы удалить маркировку клеммной группы TS-F-08 | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.9 |  | Резерв |  | DI-NIS (Diagnostic) DCS | 31.03.25 сигнал 17XAD1059 удален по TQ-126 25.07.2024 изм тег | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 22 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-F-08 клеммы 5, 6 до терм платы удалить маркировку клеммной группы TS-F-08 | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.9 |  | Резерв |  | DI-NIS (Diagnostic) DCS | 31.03.25 сигнал 17XAD1060 удален по TQ-126 25.07.2024 изм тег | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 23 | DI715-S11 | 32 |  |  | демонтировать провода от клеммной группы TS-F-08 клеммы 7, 8 до терм платы удалить маркировку клеммной группы TS-F-08 | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.3 | 17-X-D1061 | 17XAD1061 |  | DI-NIS (Diagnostic) DCS | 25.07.2024 добавлен | Сигнал | Diagnostic |  | DCS_DI_01 |  |  | 17-I-DD-N-102BL02 | 06 Pair | Pr.04 | 17-MC-DCS-007 | TS-G-06 | 7 | 8 |  | 12 | AVK 2,5 A, AVK 2,5 A |  |  | O1011200 | TUA711-DIR32 | 17-SC-DCS-002/O1011200/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011200 | 1 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | 17-SC-DCS-002 SWITCH FAILURE | 17-SC-DCS-002 | 18-AMMONIA BUILDING | 02-Control Room and Rack Room | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [23 empty] | TS-G-06:7/ O1011200:32A | TS-G-06:8/ O1011200:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 | 17-Z -100769 | 17ZSH100769 |  | DI-NIS (VFC) DCS |  | Сигнал | Position High Switch | 4124-GP-VD-BD17917K101004_SH.3 | DCS_DI_01 | Field |  | 17-C-DD-001-LP001-K101 | 12 Pair | Pr.08 | 17-MC-DCS-007 | TS-F-01 | 15 | 16 |  | 24 | AVK 2,5 A, AVK 2,5 A |  |  | O1011113 | TUA711-DIR32 | 17-SC-DCS-002/O1011113/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011113 | 14 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | FLYWHEEL LOCKING DEVICE LIMIT SWITCH | КОНЕЧН ВЫКЛ МАХОВИКА | 17-AMMONIA UTILITIES | 10-Combined Bldgn-N2 plant, Demi water | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [6 empty] | N/A | [12 empty] | TS-F-01:15/ O1011113:8A | TS-F-01:16/ O1011113:8B | [10 empty] | 8A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U5 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 5 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:5A/ O1010001_U5:5 | O1010001:5C/ O1010001_U5:6 | [6 empty] | 5A | 5C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U6 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 6 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:6A/ O1010001_U6:5 | O1010001:6C/ O1010001_U6:6 | [6 empty] | 6A | 6C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U7 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 7 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:7A/ O1010001_U7:5 | O1010001:7C/ O1010001_U7:6 | [6 empty] | 7A | 7C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U8 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 8 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:8A/ O1010001_U8:5 | O1010001:8C/ O1010001_U8:6 | [6 empty] | 8A | 8C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U9 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 9 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:9A/ O1010001_U9:5 | O1010001:9C/ O1010001_U9:6 | [6 empty] | 9A | 9C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U10 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 10 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:10A/ O1010001_U10:5 | O1010001:10C/ O1010001_U10:6 | [6 empty] | 10A | 10C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U11 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 11 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:11A/ O1010001_U11:5 | O1010001:11C/ O1010001_U11:6 | [6 empty] | 11A | 11C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U12 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 12 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:12A/ O1010001_U12:5 | O1010001:12C/ O1010001_U12:6 | [6 empty] | 12A | 12C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U13 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 13 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:13A/ O1010001_U13:5 | O1010001:13C/ O1010001_U13:6 | [6 empty] | 13A | 13C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 4 wire) DCS | 30.05.2024 сигнал/кабель удален 10.06.2024 замена типовой схемы | Резерв |  |  | DCS_AI_03 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U14 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 14 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:14A/ O1010001_U14:5 | O1010001:14C/ O1010001_U14:6 | [6 empty] | 14A | 14C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 4 wire) DCS | 30.05.2024 сигнал/кабель удален 10.06.2024 замена типовой схемы | Резерв |  |  | DCS_AI_03 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U15 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 15 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:15A/ O1010001_U15:5 | O1010001:15C/ O1010001_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 4 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_03 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010001_U16 | HD5542 | O1010001 | TUA711-AIO16 | 17-SC-DCS-001/O1010001/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010001 | 2 | 16 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010001:16A/ O1010001_U16:5 | O1010001:16C/ O1010001_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010002_U1 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 1 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010002:1A/ O1010002_U1:5 | O1010002:1C/ O1010002_U1:6 | [6 empty] | 1A | 1C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010002_U2 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 2 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010002:2A/ O1010002_U2:5 | O1010002:2C/ O1010002_U2:6 | [6 empty] | 2A | 2C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010002_U3 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 3 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010002:3A/ O1010002_U3:5 | O1010002:3C/ O1010002_U3:6 | [6 empty] | 3A | 3C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 30.05.2024 сигнал/кабель удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010002_U4 | HD5542 | O1010002 | TUA711-AIO16 | 17-SC-DCS-001/O1010002/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010002 | 3 | 4 | AI713-H11 | 16 | [5 empty] | резерв | [23 empty] | O1010002:4A/ O1010002_U4:5 | O1010002:4C/ O1010002_U4:6 | [6 empty] | 4A | 4C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 26.06.24 по TQ-061 сигнал удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010003_U10 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010003:10A/ O1010003_U10:5 | O1010003:10C/ O1010003_U10:6 | [6 empty] | 10A | 10C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 26.06.24 по TQ-061 сигнал удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010003_U11 | HD5542 | O1010003 | TUA711-AIO16 | 17-SC-DCS-001/O1010003/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010003 | 4 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010003:11A/ O1010003_U11:5 | O1010003:11C/ O1010003_U11:6 | [6 empty] | 11A | 11C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010007_U13 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010007:13A/ O1010007_U13:5 | O1010007:13C/ O1010007_U13:6 | [6 empty] | 13A | 13C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010007_U14 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010007:14A/ O1010007_U14:5 | O1010007:14C/ O1010007_U14:6 | [6 empty] | 14A | 14C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010007_U15 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010007:15A/ O1010007_U15:5 | O1010007:15C/ O1010007_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010007_U16 | HD5542 | O1010007 | TUA711-AIO16 | 17-SC-DCS-001/O1010007/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010007 | 8 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010007:16A/ O1010007_U16:5 | O1010007:16C/ O1010007_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-RTD-NIS (3 wire) DCS |  | Резерв |  |  | DCS_AI_05 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A, AVK 2,5 A | O1010008_U6 | HD5573 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:6A/ O1010008_U6:5 | O1010008:6C/ O1010008_U6:6 | [6 empty] | 6A | 6C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U7 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:7A/ O1010008_U7:5 | O1010008:7C/ O1010008_U7:6 | [6 empty] | 7A | 7C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U8 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:8A/ O1010008_U8:5 | O1010008:8C/ O1010008_U8:6 | [6 empty] | 8A | 8C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U9 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:9A/ O1010008_U9:5 | O1010008:9C/ O1010008_U9:6 | [6 empty] | 9A | 9C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U10 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:10A/ O1010008_U10:5 | O1010008:10C/ O1010008_U10:6 | [6 empty] | 10A | 10C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U11 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:11A/ O1010008_U11:5 | O1010008:11C/ O1010008_U11:6 | [6 empty] | 11A | 11C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U12 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:12A/ O1010008_U12:5 | O1010008:12C/ O1010008_U12:6 | [6 empty] | 12A | 12C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U13 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:13A/ O1010008_U13:5 | O1010008:13C/ O1010008_U13:6 | [6 empty] | 13A | 13C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U14 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:14A/ O1010008_U14:5 | O1010008:14C/ O1010008_U14:6 | [6 empty] | 14A | 14C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U15 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:15A/ O1010008_U15:5 | O1010008:15C/ O1010008_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010008_U16 | HD5542 | O1010008 | TUA711-AIO16 | 17-SC-DCS-001/O1010008/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010008 | 9 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010008:16A/ O1010008_U16:5 | O1010008:16C/ O1010008_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010009_U16 | HD5542 | O1010009 | TUA711-AIO16 | 17-SC-DCS-001/O1010009/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010009 | 10 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010009:16A/ O1010009_U16:5 | O1010009:16C/ O1010009_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010010_U9 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010010:9A/ O1010010_U9:5 | O1010010:9C/ O1010010_U9:6 | [6 empty] | 9A | 9C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010010_U10 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010010:10A/ O1010010_U10:5 | O1010010:10C/ O1010010_U10:6 | [6 empty] | 10A | 10C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010010_U11 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010010:11A/ O1010010_U11:5 | O1010010:11C/ O1010010_U11:6 | [6 empty] | 11A | 11C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010010_U12 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010010:12A/ O1010010_U12:5 | O1010010:12C/ O1010010_U12:6 | [6 empty] | 12A | 12C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010010_U13 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010010:13A/ O1010010_U13:5 | O1010010:13C/ O1010010_U13:6 | [6 empty] | 13A | 13C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010010_U14 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010010:14A/ O1010010_U14:5 | O1010010:14C/ O1010010_U14:6 | [6 empty] | 14A | 14C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010010_U15 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010010:15A/ O1010010_U15:5 | O1010010:15C/ O1010010_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010010_U16 | HD5542 | O1010010 | TUA711-AIO16 | 17-SC-DCS-001/O1010010/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010010 | 11 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010010:16A/ O1010010_U16:5 | O1010010:16C/ O1010010_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS | 26.06.24 по TQ-061 сигнал удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010011_U10 | HD5542 | O1010011 | TUA711-AIO16 | 17-SC-DCS-001/O1010011/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010011 | 12 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010011:10A/ O1010011_U10:5 | O1010011:10C/ O1010011_U10:6 | [6 empty] | 10A | 10C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS | 26.06.24 по TQ-061 сигнал удален | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010012R_U15 | HD5542 | O1010012R | TUA711-AIO16 | 17-SC-DCS-001/O1010012R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010012R | 13 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010012R:15A/ O1010012R_U15:5 | O1010012R:15C/ O1010012R_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010014R_U16 | HD5542 | O1010014R | TUA711-AIO16 | 17-SC-DCS-001/O1010014R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP011 | O1010014R | 15 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010014R:16A/ O1010014R_U16:5 | O1010014R:16C/ O1010014R_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 7 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 8 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 9 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 10 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 11 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 12 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 13 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 14 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 15 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1010100R | TUA711-AIO16 | 17-SC-DCS-001/O1010100R/ 17-MC-DCS-008 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010100R | 1 | 16 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | AI-R-IS (4-20 mA, 2 wire) DCS | 26.06.24 по TQ-061 сигнал удален | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010102R_U4 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010102R:4A/ O1010102R_U4:5 | O1010102R:4C/ O1010102R_U4:6 | [6 empty] | 4A | 4C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010102R_U15 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010102R:15A/ O1010102R_U15:5 | O1010102R:15C/ O1010102R_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-IS (4-20 mA, 4 wire) DCS |  | Резерв |  |  | DCS_AI_04 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010102R_U16 | HD5542 | O1010102R | TUA711-AIO16 | 17-SC-DCS-001/O1010102R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010102R | 3 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010102R:16A/ O1010102R_U16:5 | O1010102R:16C/ O1010102R_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010106R_U12 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 12 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010106R:12A/ O1010106R_U12:5 | O1010106R:12C/ O1010106R_U12:6 | [6 empty] | 12A | 12C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010106R_U13 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 13 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010106R:13A/ O1010106R_U13:5 | O1010106R:13C/ O1010106R_U13:6 | [6 empty] | 13A | 13C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010106R_U14 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 14 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010106R:14A/ O1010106R_U14:5 | O1010106R:14C/ O1010106R_U14:6 | [6 empty] | 14A | 14C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010106R_U15 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 15 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010106R:15A/ O1010106R_U15:5 | O1010106R:15C/ O1010106R_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010106R_U16 | HD5546 | O1010106R | TUA711-AIO16 | 17-SC-DCS-001/O1010106R/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010106R | 7 | 16 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010106R:16A/ O1010106R_U16:5 | O1010106R:16C/ O1010106R_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | AO-R-IS (4-20 mA) DCS | 26.06.24 по TQ-061 сигнал удален | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010110R_U2 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 2 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010110R:2A/ O1010110R_U2:5 | O1010110R:2C/ O1010110R_U2:6 | [6 empty] | 2A | 2C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | AO-R-IS (4-20 mA) DCS | 26.06.24 по TQ-061 сигнал удален | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010110R_U8 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 8 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010110R:8A/ O1010110R_U8:5 | O1010110R:8C/ O1010110R_U8:6 | [6 empty] | 8A | 8C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | AO-R-IS (4-20 mA) DCS | 26.06.24 по TQ-061 сигнал удален | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010110R_U9 | HD5546 | O1010110R | TUA711-AIO16 | 17-SC-DCS-001/O1010110R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010110R | 11 | 9 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010110R:9A/ O1010110R_U9:5 | O1010110R:9C/ O1010110R_U9:6 | [6 empty] | 9A | 9C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-IS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010112R_U2 | HD5546 | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 2 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010112R:2A/ O1010112R_U2:5 | O1010112R:2C/ O1010112R_U2:6 | [6 empty] | 2A | 2C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-IS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010112R_U3 | HD5546 | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 3 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010112R:3A/ O1010112R_U3:5 | O1010112R:3C/ O1010112R_U3:6 | [6 empty] | 3A | 3C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-IS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010112R_U4 | HD5546 | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 4 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010112R:4A/ O1010112R_U4:5 | O1010112R:4C/ O1010112R_U4:6 | [6 empty] | 4A | 4C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-IS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010112R_U5 | HD5546 | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 5 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010112R:5A/ O1010112R_U5:5 | O1010112R:5C/ O1010112R_U5:6 | [6 empty] | 5A | 5C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 6 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 7 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 8 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 9 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 10 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 11 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 12 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 13 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 14 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 15 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1010112R | TUA711-AIO16 | 17-SC-DCS-001/O1010112R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010112R | 13 | 16 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010114_U5 | HD5546 | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 5 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010114:5A/ O1010114_U5:5 | O1010114:5C/ O1010114_U5:6 | [6 empty] | 5A | 5C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 6 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 7 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 8 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 9 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 10 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 11 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 12 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 13 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 14 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 15 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1010114 | TUA711-AIO16 | 17-SC-DCS-001/O1010114/ 17-MC-DCS-006 |  | 17-SC-DCS-001 | CPO101 | 0 | BP012 | O1010114 | 15 | 16 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.8 | 17-X -15005 | 17XS15005 |  | DI-NIS (VFC) DCS | 24.03.25 сигнал перенесен из WTU по TQ-122 | Сигнал | Motor running indication | 4124-FY-VD-BD17717L18100002_SH.2 | DCS_DI_01 | LP |  | 17-XS-15005 | 02 Pair | Pr.01 | 17-MC-DCS-001 | TS-F-07 | 1 | 2 |  | 4 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 31 | DI715-S11 | 32 |  |  | смонтировать новую клеммную группу, провода от клемм до терм платы | DCS AMMONIA-UTILITIES | 17-L181 RUNNING | 17-L181 РАБОТАЕТ | 17-AMMONIA UTILITIES | 15-Water Preparation Unit | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-07:1/ O1010200:31A | TS-F-07:2/ O1010200:31B | [10 empty] | 31A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
02.8 | 17-X -15005 | 17XSA15005 |  | DI-NIS (VFC) DCS | 24.03.25 сигнал перенесен из WTU по TQ-122 | Сигнал | Heater available indication | 4124-FY-VD-BD17717L18100002_SH.2 | DCS_DI_01 | LP |  | 17-XS-15005 | 02 Pair | Pr.02 | 17-MC-DCS-001 | TS-F-07 | 3 | 4 |  | 4 | AVK 2,5 A, AVK 2,5 A |  |  | O1010200 | TUA711-DIR32 | 17-SC-DCS-001/O1010200/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010200 | 1 | 32 | DI715-S11 | 32 |  |  | смонтировать новую клеммную группу, провода от клемм до терм платы | DCS AMMONIA-UTILITIES | 17-L181 LCP FAULT | 17-НЕИСПРАВНОСТЬ LCP L181 | 17-AMMONIA UTILITIES | 15-Water Preparation Unit | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | --- |  |  | 3000/4000 MTPD Ammonia / Urea & Granulation Plants | [19 empty] | TS-F-07:3/ O1010200:32A | TS-F-07:4/ O1010200:32B | [10 empty] | 32A | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010202 | TUA711-DIR32 | 17-SC-DCS-001/O1010202/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010202 | 3 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010203_U24 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010203:24A/ O1010203_U24:5 | O1010203:24B/ O1010203_U24:6 | [6 empty] | 24A | 24B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010203_U25 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010203:25A/ O1010203_U25:5 | O1010203:25B/ O1010203_U25:6 | [6 empty] | 25A | 25B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010203_U26 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010203:26A/ O1010203_U26:5 | O1010203:26B/ O1010203_U26:6 | [6 empty] | 26A | 26B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010203_U27 | HD5516 | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010203:27A/ O1010203_U27:5 | O1010203:27B/ O1010203_U27:6 | [6 empty] | 27A | 27B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Conductivity) DCS |  | Резерв |  |  | DCS_DI_04 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010203_U29 | KFD2-ER-1.W.LB | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010203:29A/ O1010203_U29:7 | O1010203:29B/ O1010203_U29:8 | [6 empty] | 29A | 29B |  |  |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Conductivity) DCS |  | Резерв |  |  | DCS_DI_04 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010203_U30 | KFD2-ER-1.W.LB | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010203:30A/ O1010203_U30:7 | O1010203:30B/ O1010203_U30:8 | [6 empty] | 30A | 30B |  |  |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Conductivity) DCS |  | Резерв |  |  | DCS_DI_04 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010203_U31 | KFD2-ER-1.W.LB | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010203:31A/ O1010203_U31:7 | O1010203:31B/ O1010203_U31:8 | [6 empty] | 31A | 31B |  |  |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Conductivity) DCS |  | Резерв |  |  | DCS_DI_04 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010203_U32 | KFD2-ER-1.W.LB | O1010203 | TUA711-DIO32 | 17-SC-DCS-001/O1010203/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010203 | 4 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010203:32A/ O1010203_U32:7 | O1010203:32B/ O1010203_U32:8 | [6 empty] | 32A | 32B |  |  |  | 7 | 8 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-NIS |  | Пустой | [8 empty] | 17-MC-DCS-002 | [8 empty] | O1010204 |  | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-NIS |  | Пустой | [8 empty] | 17-MC-DCS-002 | [8 empty] | O1010204 |  | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-NIS |  | Пустой | [8 empty] | 17-MC-DCS-002 | [8 empty] | O1010204 |  | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-NIS |  | Пустой | [8 empty] | 17-MC-DCS-002 | [8 empty] | O1010204 |  | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-NIS |  | Пустой | [8 empty] | 17-MC-DCS-002 | [8 empty] | O1010204 |  | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-NIS |  | Пустой | [8 empty] | 17-MC-DCS-002 | [8 empty] | O1010204 |  | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-NIS |  | Пустой | [8 empty] | 17-MC-DCS-002 | [8 empty] | O1010204 |  | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010204 | TUA711-DIR32 | 17-SC-DCS-001/O1010204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010204 | 5 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U9 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 9 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:9A/ O1010205_U9:5 | O1010205:9B/ O1010205_U9:6 | [6 empty] | 9A | 9B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U10 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 10 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:10A/ O1010205_U10:5 | O1010205:10B/ O1010205_U10:6 | [6 empty] | 10A | 10B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U11 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 11 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:11A/ O1010205_U11:5 | O1010205:11B/ O1010205_U11:6 | [6 empty] | 11A | 11B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U12 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 12 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:12A/ O1010205_U12:5 | O1010205:12B/ O1010205_U12:6 | [6 empty] | 12A | 12B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U13 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 13 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:13A/ O1010205_U13:5 | O1010205:13B/ O1010205_U13:6 | [6 empty] | 13A | 13B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U14 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 14 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:14A/ O1010205_U14:5 | O1010205:14B/ O1010205_U14:6 | [6 empty] | 14A | 14B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U15 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 15 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:15A/ O1010205_U15:5 | O1010205:15B/ O1010205_U15:6 | [6 empty] | 15A | 15B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U16 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 16 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:16A/ O1010205_U16:5 | O1010205:16B/ O1010205_U16:6 | [6 empty] | 16A | 16B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U17 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 17 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:17A/ O1010205_U17:5 | O1010205:17B/ O1010205_U17:6 | [6 empty] | 17A | 17B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U18 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 18 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:18A/ O1010205_U18:5 | O1010205:18B/ O1010205_U18:6 | [6 empty] | 18A | 18B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U19 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 19 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:19A/ O1010205_U19:5 | O1010205:19B/ O1010205_U19:6 | [6 empty] | 19A | 19B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U20 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 20 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:20A/ O1010205_U20:5 | O1010205:20B/ O1010205_U20:6 | [6 empty] | 20A | 20B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U21 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 21 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:21A/ O1010205_U21:5 | O1010205:21B/ O1010205_U21:6 | [6 empty] | 21A | 21B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U22 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 22 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:22A/ O1010205_U22:5 | O1010205:22B/ O1010205_U22:6 | [6 empty] | 22A | 22B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U23 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 23 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:23A/ O1010205_U23:5 | O1010205:23B/ O1010205_U23:6 | [6 empty] | 23A | 23B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U24 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 24 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:24A/ O1010205_U24:5 | O1010205:24B/ O1010205_U24:6 | [6 empty] | 24A | 24B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U25 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 25 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:25A/ O1010205_U25:5 | O1010205:25B/ O1010205_U25:6 | [6 empty] | 25A | 25B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U26 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 26 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:26A/ O1010205_U26:5 | O1010205:26B/ O1010205_U26:6 | [6 empty] | 26A | 26B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U27 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 27 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:27A/ O1010205_U27:5 | O1010205:27B/ O1010205_U27:6 | [6 empty] | 27A | 27B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U28 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 28 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:28A/ O1010205_U28:5 | O1010205:28B/ O1010205_U28:6 | [6 empty] | 28A | 28B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U29 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 29 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:29A/ O1010205_U29:5 | O1010205:29B/ O1010205_U29:6 | [6 empty] | 29A | 29B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U30 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 30 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:30A/ O1010205_U30:5 | O1010205:30B/ O1010205_U30:6 | [6 empty] | 30A | 30B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U31 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 31 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:31A/ O1010205_U31:5 | O1010205:31B/ O1010205_U31:6 | [6 empty] | 31A | 31B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1010205_U32 | HD5516 | O1010205 | TUA711-DIO32 | 17-SC-DCS-001/O1010205/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010205 | 6 | 32 | DI715-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1010205:32A/ O1010205_U32:5 | O1010205:32B/ O1010205_U32:6 | [6 empty] | 32A | 32B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010208 | TUA711-DIO32 | 17-SC-DCS-001/O1010208/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010208 | 9 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1010211 | TUA711-DOR32 | 17-SC-DCS-001/O1010211/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010211 | 12 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010215 | TUA711-DIO32 | 17-SC-DCS-001/O1010215/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP021 | O1010215 | 16 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010300 | TUA711-DIO32 | 17-SC-DCS-001/O1010300/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010300 | 1 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS |  | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS |  | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS |  | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1010301 | TUA711-DIO32 | 17-SC-DCS-001/O1010301/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010301 | 2 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011000_U7 | HD5542 | O1011000 | TUA711-AIO16 | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011000:7A/ O1011000_U7:5 | O1011000:7C/ O1011000_U7:6 | [6 empty] | 7A | 7C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-006 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011000_U8 | HD5542 | O1011000 | TUA711-AIO16 | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011000:8A/ O1011000_U8:5 | O1011000:8C/ O1011000_U8:6 | [6 empty] | 8A | 8C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-NIS | 10.06.2024 Корректировка резерва | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011000 |  | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | Пустой | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-NIS | 10.06.2024 Корректировка резерва | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011000 |  | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | Пустой | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-NIS | 10.06.2024 Корректировка резерва | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011000 |  | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | Пустой | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-NIS | 10.06.2024 Корректировка резерва | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011000 |  | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | Пустой | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-NIS | 10.06.2024 Корректировка резерва | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011000 |  | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | Пустой | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-NIS | 10.06.2024 Корректировка резерва | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011000 |  | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | Пустой | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-NIS | 10.06.2024 Корректировка резерва | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011000 |  | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | Пустой | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-NIS | 10.06.2024 Корректировка резерва | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011000 |  | 17-SC-DCS-002/O1011000/ 17-MC-DCS-006 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011000 | 1 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | Пустой | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 24.09.24 сигнал 17ZTM072LPA удален по TQ_ALL_81 | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011001_U11 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 11 | AI713-H11 | 16 |  |  | демонтировать провода с клеммника TS-O-04 (клеммы 3, 4) до барьера | DCS AMMONIA-UTILITIES | [25 empty] | O1011001:11A/ O1011001_U11:5 | O1011001:11C/ O1011001_U11:6 | [6 empty] | 11A | 11C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 24.09.24 сигнал 17ZTM072LPB удален по TQ_ALL_81 | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011002_U10 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 10 | AI713-H11 | 16 |  |  | демонтировать провода с клеммника TS-O-04 (клеммы 5, 6) до барьера | DCS AMMONIA-UTILITIES | [25 empty] | O1011002:10A/ O1011002_U10:5 | O1011002:10C/ O1011002_U10:6 | [6 empty] | 10A | 10C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 24.09.24 сигнал 17ZTM073LPA удален по TQ_ALL_81 | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011001_U16 | HD5542 | O1011001 | TUA711-AIO16 | 17-SC-DCS-002/O1011001/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011001 | 2 | 16 | AI713-H11 | 16 |  |  | демонтировать провода с клеммника TS-O-07 (клеммы 3, 4) до барьера | DCS AMMONIA-UTILITIES | [25 empty] | O1011001:16A/ O1011001_U16:5 | O1011001:16C/ O1011001_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | AI-NIS (4-20 mA, 2 wire) DCS | 24.09.24 сигнал 17ZTM073LPB удален по TQ_ALL_81 | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011002_U16 | HD5542 | O1011002 | TUA711-AIO16 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011002 | 3 | 16 | AI713-H11 | 16 |  |  | демонтировать провода с клеммника TS-O-07 (клеммы 3, 4) до барьера | DCS AMMONIA-UTILITIES | [25 empty] | O1011002:16A/ O1011002_U16:5 | O1011002:16C/ O1011002_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011005_U10 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011005:10A/ O1011005_U10:5 | O1011005:10C/ O1011005_U10:6 | [6 empty] | 10A | 10C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011005_U12 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011005:12A/ O1011005_U12:5 | O1011005:12C/ O1011005_U12:6 | [6 empty] | 12A | 12C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011005_U13 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011005:13A/ O1011005_U13:5 | O1011005:13C/ O1011005_U13:6 | [6 empty] | 13A | 13C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011005_U14 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011005:14A/ O1011005_U14:5 | O1011005:14C/ O1011005_U14:6 | [6 empty] | 14A | 14C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011005_U15 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011005:15A/ O1011005_U15:5 | O1011005:15C/ O1011005_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011005_U16 | HD5542 | O1011005 | TUA711-AIO16 | 17-SC-DCS-002/O1011005/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011005 | 6 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011005:16A/ O1011005_U16:5 | O1011005:16C/ O1011005_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS | 26.06.24 по TQ-061 сигнал удален | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011006_U2 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [25 empty] | O1011006:2A/ O1011006_U2:5 | O1011006:2C/ O1011006_U2:6 | [6 empty] | 2A | 2C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011006_U15 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011006:15A/ O1011006_U15:5 | O1011006:15C/ O1011006_U15:6 | [6 empty] | 15A | 15C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_01 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011006_U16 | HD5542 | O1011006 | TUA711-AIO16 | 17-SC-DCS-002/O1011006/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011006 | 7 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011006:16A/ O1011006_U16:5 | O1011006:16C/ O1011006_U16:6 | [6 empty] | 16A | 16C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (PI converter, 3 wire) DCS |  | Резерв |  |  | DCS_PI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U3 | GS8555-EX | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:3A/ O1011008R_U3:3 | O1011008R:3C/ O1011008R_U3:4 | [6 empty] | 3A | 3C |  |  |  | 3 | 4 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 4 wire) DCS |  | Резерв |  |  | DCS_AI_04 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U4 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:4A/ O1011008R_U4:5 | O1011008R:4C/ O1011008R_U4:6 | [6 empty] | 4A | 4C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U5 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:5A/ O1011008R_U5:5 | O1011008R:5C/ O1011008R_U5:6 | [6 empty] | 5A | 5C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U6 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:6A/ O1011008R_U6:5 | O1011008R:6C/ O1011008R_U6:6 | [6 empty] | 6A | 6C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U7 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:7A/ O1011008R_U7:5 | O1011008R:7C/ O1011008R_U7:6 | [6 empty] | 7A | 7C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U8 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:8A/ O1011008R_U8:5 | O1011008R:8C/ O1011008R_U8:6 | [6 empty] | 8A | 8C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U9 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:9A/ O1011008R_U9:5 | O1011008R:9C/ O1011008R_U9:6 | [6 empty] | 9A | 9C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U10 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:10A/ O1011008R_U10:5 | O1011008R:10C/ O1011008R_U10:6 | [6 empty] | 10A | 10C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U11 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:11A/ O1011008R_U11:5 | O1011008R:11C/ O1011008R_U11:6 | [6 empty] | 11A | 11C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U12 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:12A/ O1011008R_U12:5 | O1011008R:12C/ O1011008R_U12:6 | [6 empty] | 12A | 12C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U13 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:13A/ O1011008R_U13:5 | O1011008R:13C/ O1011008R_U13:6 | [6 empty] | 13A | 13C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-NIS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011008R_U14 | HD5542 | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011008R:14A/ O1011008R_U14:5 | O1011008R:14C/ O1011008R_U14:6 | [6 empty] | 14A | 14C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-007 | [8 empty] | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-007 | [8 empty] | O1011008R | TUA711-AIO16 | 17-SC-DCS-002/O1011008R/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011008R | 9 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 |  | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 15 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1011010R | TUA711-AIO16 | 17-SC-DCS-002/O1011010R/ 17-MC-DCS-008 |  | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011010R | 11 | 16 | AI713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 |  | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 13 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 |  | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 14 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 |  | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 15 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-006 | [8 empty] | O1011012R | TUA711-AIO16 | 17-SC-DCS-002/O1011012R/ 17-MC-DCS-006 |  | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011012R | 13 | 16 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1011014R | TUA711-AIO16 | 17-SC-DCS-002/O1011014R/ 17-MC-DCS-008 |  | 17-SC-DCS-002 | CPO101 | 1 | BP011 | O1011014R | 15 | 16 | AO713-H11 | 16 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.3 |  | Резерв |  | DI-NIS (VFC) DCS | 25.07.2024 удален кабель 17-C-DD-N-001FL15 по TQ_074 | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [8 empty] | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.3 |  | Резерв |  | DI-NIS (VFC) DCS | 25.07.2024 удален кабель 17-C-DD-N-001FL15 по TQ_074 | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [8 empty] | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.3 |  | Резерв |  | DI-NIS (VFC) DCS | 25.07.2024 удален кабель 17-C-DD-N-001FL15 по TQ_074 | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [8 empty] | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011105 | TUA711-DIR32 | 17-SC-DCS-002/O1011105/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011105 | 6 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011110_U25 | HD5516 | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011110:25A/ O1011110_U25:5 | O1011110:25B/ O1011110_U25:6 | [6 empty] | 25A | 25B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011110_U26 | HD5516 | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011110:26A/ O1011110_U26:5 | O1011110:26B/ O1011110_U26:6 | [6 empty] | 26A | 26B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011110_U27 | HD5516 | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011110:27A/ O1011110_U27:5 | O1011110:27B/ O1011110_U27:6 | [6 empty] | 27A | 27B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Thermistors PTC) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011110_U28 | HD5516 | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011110:28A/ O1011110_U28:5 | O1011110:28B/ O1011110_U28:6 | [6 empty] | 28A | 28B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Thermistors PTC) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011110_U29 | HD5516 | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011110:29A/ O1011110_U29:5 | O1011110:29B/ O1011110_U29:6 | [6 empty] | 29A | 29B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Thermistors PTC) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011110_U30 | HD5516 | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011110:30A/ O1011110_U30:5 | O1011110:30B/ O1011110_U30:6 | [6 empty] | 30A | 30B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Thermistors PTC) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-004 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011110_U31 | HD5516 | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011110:31A/ O1011110_U31:5 | O1011110:31B/ O1011110_U31:6 | [6 empty] | 31A | 31B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011110 | TUA711-DIO32 | 17-SC-DCS-002/O1011110/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011110 | 11 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DI_03 | [5 empty] | 17-MC-DCS-005 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011112 | TUA711-DIO32 | 17-SC-DCS-002/O1011112/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011112 | 13 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (VFC) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-NIS |  | Пустой | [8 empty] | 17-MC-DCS-007 | [8 empty] | O1011114 |  | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-NIS |  | Пустой | [8 empty] | 17-MC-DCS-007 | [8 empty] | O1011114 |  | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-IS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011115_U20 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011115:20A/ O1011115_U20:5 | O1011115:20B/ O1011115_U20:6 | [6 empty] | 20A | 20B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-IS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011115_U21 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011115:21A/ O1011115_U21:5 | O1011115:21B/ O1011115_U21:6 | [6 empty] | 21A | 21B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-IS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011115_U22 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011115:22A/ O1011115_U22:5 | O1011115:22B/ O1011115_U22:6 | [6 empty] | 22A | 22B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-IS (NAMUR) DCS |  | Резерв |  |  | DCS_DI_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011115_U23 | HD5516 | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011115:23A/ O1011115_U23:5 | O1011115:23B/ O1011115_U23:6 | [6 empty] | 23A | 23B |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 |  | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 28 | DI715-S11 | 32 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 |  | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 29 | DI715-S11 | 32 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 |  | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 30 | DI715-S11 | 32 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 |  | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 31 | DI715-S11 | 32 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | DI-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011115 | TUA711-DIO32 | 17-SC-DCS-002/O1011115/ 17-MC-DCS-009 |  | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011115 | 16 | 32 | DI715-S11 | 32 | [46 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Diagnostic) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Diagnostic) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011114 | TUA711-DIR32 | 17-SC-DCS-002/O1011114/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP012 | O1011114 | 15 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Diagnostic) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Diagnostic) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Diagnostic) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Diagnostic) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Diagnostic) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DI-NIS (Diagnostic) DCS |  | Резерв |  |  | DCS_DI_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011201 | TUA711-DIR32 | 17-SC-DCS-002/O1011201/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011201 | 2 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | DO-NIS (24VDC) DCS | 24.09.24 сигнал 17XYST1M072LPB, кабель удалены по TQ_ALL_81 | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 11 | DO716-S11 | 32 |  |  | демонтировать провода от клеммника TS-O-02 (клемы 5, 6) до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | DO-NIS (24VDC) DCS | 24.09.24 сигнал 17XYST2M072LPB, кабель удалены по TQ_ALL_81 | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 12 | DO716-S11 | 32 |  |  | демонтировать провода от клеммника TS-O-02 (клемы 7, 8) до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | DO-NIS (24VDC) DCS | 24.09.24 сигнал 17XYST1M073LPA, кабель удалены по TQ_ALL_81 | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 13 | DO716-S11 | 32 |  |  | демонтировать провода от клеммника TS-O-02 (клемы 9, 10) до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | DO-NIS (24VDC) DCS | 24.09.24 сигнал 17XYST2M073LPA, кабель удалены по TQ_ALL_81 | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 14 | DO716-S11 | 32 |  |  | демонтировать провода от клеммника TS-O-02 (клемы 11, 12) до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | DO-NIS (24VDC) DCS | 24.09.24 сигнал 17XYST1M073LPB, кабель удалены по TQ_ALL_81 | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 15 | DO716-S11 | 32 |  |  | демонтировать провода от клеммника TS-O-02 (клемы 13, 14) до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.5 |  | Резерв |  | DO-NIS (24VDC) DCS | 24.09.24 сигнал 17XYST2M073LPB, кабель удалены по TQ_ALL_81 | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011202 | TUA711-DOR32 | 17-SC-DCS-002/O1011202/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011202 | 3 | 16 | DO716-S11 | 32 |  |  | демонтировать провода от клеммника TS-O-02 (клемы 15, 16) до терм платы | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-002 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011204 | TUA711-DOR32 | 17-SC-DCS-002/O1011204/ 17-MC-DCS-002 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011204 | 5 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS |  | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-004 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011208 | TUA711-DIO32 | 17-SC-DCS-002/O1011208/ 17-MC-DCS-004 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011208 | 9 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011210 | TUA711-DOR32 | 17-SC-DCS-002/O1011210/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011210 | 11 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 12 | DO716-S11 | 32 |  | переподключены сигналы (кабель 17-C-DD-N-001FL11-AH001) |  | DCS AMMONIA-UTILITIES |  | Резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 13 | DO716-S11 | 32 |  | переподключены сигналы (кабель 17-C-DD-N-001FL11-AH001) |  | DCS AMMONIA-UTILITIES |  | Резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (VFC NO) DCS |  | Резерв |  |  | DCS_DO_02 | [5 empty] | 17-MC-DCS-007 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011211 | TUA711-DOR32 | 17-SC-DCS-002/O1011211/ 17-MC-DCS-007 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011211 | 12 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 9 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 10 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 11 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 12 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 13 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 14 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 15 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 16 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 17 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 18 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 19 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 20 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 21 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 22 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 23 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 24 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 25 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 26 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 27 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 28 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 29 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 30 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 31 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (24VDC) DCS |  | Резерв |  |  | DCS_DO_01 | [5 empty] | 17-MC-DCS-001 | [5 empty] | AVK 2,5 A, AVK 2,5 A |  |  | O1011212 | TUA711-DOR32 | 17-SC-DCS-002/O1011212/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011212 | 13 | 32 | DO716-S11 | 32 |  | терм панель перенесена из 17-MC-DCS-002 |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 3 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 4 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 5 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 6 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 7 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 8 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 9 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 10 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 11 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 12 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 13 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 14 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 15 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 16 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 17 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 18 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 19 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 20 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 21 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 22 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 23 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 24 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 25 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 26 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 230VAC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_03 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 27 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 220VDC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_04 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 28 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 220VDC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_04 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 29 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 220VDC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_04 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 30 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 220VDC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_04 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 31 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | DO-NIS (MCC 220VDC) DCS | 14.06.2024 перенос из шкафа 005 | Резерв |  |  | DCS_DO_04 | [5 empty] | 17-MC-DCS-003 | [5 empty] | ASK 3MLD, ASK 3MB |  |  | O1011213 | TUA711-DIO32 | 17-SC-DCS-002/O1011213/ 17-MC-DCS-003 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP021 | O1011213 | 14 | 32 | DO716-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011300R_U1 | HD5542 | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 1 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011300R:1A/ O1011300R_U1:5 | O1011300R:1C/ O1011300R_U1:6 | [6 empty] | 1A | 1C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AI-R-IS (4-20 mA, 2 wire) DCS |  | Резерв |  |  | DCS_AI_02 | [5 empty] | 17-MC-DCS-009 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011300R_U2 | HD5542 | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 2 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011300R:2A/ O1011300R_U2:5 | O1011300R:2C/ O1011300R_U2:6 | [6 empty] | 2A | 2C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 3 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 4 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 5 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 6 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 7 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 8 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 9 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 10 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 11 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 12 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 13 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 14 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 15 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AI-R-IS |  | Пустой | [8 empty] | 17-MC-DCS-009 | [8 empty] | O1011300R | TUA711-AIO16 | 17-SC-DCS-002/O1011300R/ 17-MC-DCS-009 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011300R | 1 | 16 | AI713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011302R_U1 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 1 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011302R:1A/ O1011302R_U1:5 | O1011302R:1C/ O1011302R_U1:6 | [6 empty] | 1A | 1C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011302R_U2 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 2 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011302R:2A/ O1011302R_U2:5 | O1011302R:2C/ O1011302R_U2:6 | [6 empty] | 2A | 2C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011302R_U3 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 3 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011302R:3A/ O1011302R_U3:5 | O1011302R:3C/ O1011302R_U3:6 | [6 empty] | 3A | 3C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011302R_U4 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 4 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011302R:4A/ O1011302R_U4:5 | O1011302R:4C/ O1011302R_U4:6 | [6 empty] | 4A | 4C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011302R_U5 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 5 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011302R:5A/ O1011302R_U5:5 | O1011302R:5C/ O1011302R_U5:6 | [6 empty] | 5A | 5C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011302R_U6 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 6 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011302R:6A/ O1011302R_U6:5 | O1011302R:6C/ O1011302R_U6:6 | [6 empty] | 6A | 6C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011302R_U7 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 7 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011302R:7A/ O1011302R_U7:5 | O1011302R:7C/ O1011302R_U7:6 | [6 empty] | 7A | 7C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011302R_U8 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 8 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011302R:8A/ O1011302R_U8:5 | O1011302R:8C/ O1011302R_U8:6 | [6 empty] | 8A | 8C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Резерв |  | AO-R-NIS (4-20 mA) DCS |  | Резерв |  |  | DCS_AO_02 | [5 empty] | 17-MC-DCS-008 | [5 empty] | AVK 2,5 A, AVK 2,5 A | O1011302R_U9 | HD5546 | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 9 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [23 empty] | O1011302R:9A/ O1011302R_U9:5 | O1011302R:9C/ O1011302R_U9:6 | [6 empty] | 9A | 9C |  |  |  | 5 | 6 |  |  | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 12 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 13 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 14 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 15 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
01 |  | Пустой |  | AO-R-NIS |  | Пустой | [8 empty] | 17-MC-DCS-008 | [8 empty] | O1011302R | TUA711-AIO16 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011302R | 3 | 16 | AO713-H11 | 16 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 1 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 2 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 3 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 4 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 5 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 6 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 7 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.1 |  | Резерв |  | DI-NIS (MCC 220VDC) DCS | 04.07.2024 Добавил резервный модуль для DI_05 | Резерв |  |  | DCS_DI_05 | [5 empty] | 17-MC-DCS-005 | [8 empty] | O1011304 | TUA711-DIO32 | 17-SC-DCS-002/O1011304/ 17-MC-DCS-005 | DB37-*m | 17-SC-DCS-002 | CPO101 | 1 | BP022 | O1011304 | 5 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES |  | резерв | [40 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.4 |  | Резерв |  | DI-NIS (24VDC) DCS | 06.08.2024 добавлен резервированный модуль | Резерв |  |  | DCS_DI_07 | [5 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R | TUA711-DIR32 | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 8 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.4 |  | Резерв |  | DI-NIS (24VDC) DCS | 06.08.2024 добавлен резервированный модуль | Резерв |  |  | DCS_DI_07 | [5 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R | TUA711-DIR32 | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 9 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES | [42 empty] | #NAME? | #NAME? | #NAME? | #NAME?
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 10 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 11 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 12 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 13 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 14 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 15 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 16 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 17 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 18 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 19 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 20 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 21 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 22 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 23 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 24 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 25 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 26 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 27 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 28 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 29 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 30 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 31 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
02.4 |  | Пустой |  |  | 06.08.2024 добавлен резервированный модуль | Пустой | [8 empty] | 17-MC-DCS-001 | [8 empty] | O1010304R |  | 17-SC-DCS-001/O1010304R/ 17-MC-DCS-001 | DB37-*m | 17-SC-DCS-001 | CPO101 | 0 | BP022 | O1010304R | 5 | 32 | DI715-S11 | 32 |  |  |  | DCS AMMONIA-UTILITIES
[83 empty] | #NAME? | #NAME? | #NAME? | #NAME?

## Для сигналов Eplan
CABINET_MAR | FTS_NAME | FTS_TERM1 | TAG | CLASS_TYPE_SIG | IO type (Типовая схема подключения) | CABINET_SYS | MODULE | MODULE_TYPE | SYS_CABLE | STB_NAME | STB_PART | сцеп1 | сцеп2 | сцеп3 | сцеп4 | Доп. поле [17] ru_RU | Доп. поле [18] ru_RU | BARRIER_NAME | BARRIER_MODEL | Доп. поле [13] ru_RU | Доп. поле [14] ru_RU | от полевой клеммы до барьера белый | от полевой клеммы до барьера черный | от полевой клеммы до барьера черный 2 | Доп. поле [15] ru_RU
17-MC-DCS-008 | TS-O-07 | 1 | 17LT07063 | AI-NIS (4-20 mA, 2 wire) DCS | DCS_AI_01 | 17-SC-DCS-002 | O1011002 | AI713-H11 | 17-SC-DCS-002/O1011002/ 17-MC-DCS-008 | O1011002 | TUA711-AIO16 | 15A | 15C | O1011002:15A/ O1011002_U15:5 | O1011002:15C/ O1011002_U15:6 | 5 | 6 | O1011002_U15 | HD5542 | 3 | 4 | TS-O-07:1/ O1011002_U15:3 | TS-O-07:2/ O1011002_U15:4
17-MC-DCS-008 | TS-O-07 | 3 | 17-HY-070855 | AO-R-NIS (4-20 mA) DCS | DCS_AO_02 | 17-SC-DCS-002 | O1011302R | AO713-H11 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | O1011302R | TUA711-AIO16 | 10A | 10C | O1011302R:10A/ O1011302R_U10:5 | O1011302R:10C/ O1011302R_U10:6 | 5 | 6 | O1011302R_U10 | HD5546 | 3 | 4 | TS-O-07:3/ O1011302R_U10:3 | TS-O-07:4/ O1011302R_U10:4
17-MC-DCS-008 | TS-O-07 | 5 | 17-HY-070856 | AO-R-NIS (4-20 mA) DCS | DCS_AO_02 | 17-SC-DCS-002 | O1011302R | AO713-H11 | 17-SC-DCS-002/O1011302R/ 17-MC-DCS-008 | O1011302R | TUA711-AIO16 | 11A | 11C | O1011302R:11A/ O1011302R_U11:5 | O1011302R:11C/ O1011302R_U11:6 | 5 | 6 | O1011302R_U11 | HD5546 | 3 | 4 | TS-O-07:5/ O1011302R_U11:3 | TS-O-07:6/ O1011302R_U11:4

## Для сигналов Eplan2
CABINET_MAR | FTS_NAME | CAB_NAME | FTS_TYPE
17-MC-DCS-008 | TS-O-01 | 17-C-AD-N-001FL03-L022 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-O-02 | 17-C-AD-N-001FL17 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-O-03 | 17-C-AD-N-002FL03-L022 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-O-04 | 17-C-AD-N-002FL07-L073 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-O-05 | 17-C-AD-N-002FL14 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-O-06 | 17-C-AD-N-003FL03-L022 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-O-07 | 17-C-AD-N-003FL07-L073 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-O-08 | 17-C-AD-N-004FL07-L073 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-O-09 | 17-C-AD-N-005FL03-L022 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-P-01 | 17-C-AD-N-002FL10 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-P-02 | 17-C-AD-N-002FL11-L111 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-P-03 | 17-C-AD-N-006FL03-L022 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-P-04 | 17-C-AD-N-003FL11-L111 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-P-05 | 17-LT-03001 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-P-06 | 17-С-AD-N-1-FL90 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-P-07 | 17-TT -11264 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | TS-Q-01 | 17-PT-11287 | AVK 2,5 A, AVK 2,5 A
17-MC-DCS-008 | (пусто) | (пусто)
17-MC-DCS-008 | (пусто) | (пусто) | AVK 2,5 A, AVK 2,5 A

## Проверки
|  |  | MODULE | Канальность
MODULE | SLOT | CABINET_SYS | (пусто) | (пусто) |  |  | CAB_NAME | CAB_TYPE | FTS_NAME | CABINET_MAR | CAB_NAME | Set_Name | Количество по полю TAG | CAB_TYPE | MAX TERMINAL | Set_Name | FTS_TERM1 | FTS_TERM2 | FTS_TERM3 | CLASS_TYPE_SIG | FTS_TYPE | MODULE | SLOT | RACK | CABINET_MAR | MODULE | SLOT | Сумма по полю CHANNEL
O1010000 | 1 | 17-SC-DCS-001 | O1010000 | 16 | CLASS_TYPE_SIG | MODULE_TYPE | 10-FSH-08003 | 01 Pair | TS-Q-05 | 17-MC-DCS-002 | 10-FSH-08003 | Pr.01 | 1 | 01 Pair | 2 | C.01 | 1 | 2 |  | AI-IS (4-20 mA, 2 wire) DCS | AVK 2,5 A, AVK 2,5 A | O1010000 | 1 | BP011 | 17-MC-DCS-006 | (пусто) | (пусто)
O1010001 | 2 | 17-SC-DCS-001 | O1010001 | 16 | AI-IS (4-20 mA, 2 wire) DCS | AI713-H11 | 10-FSH-08007 | 01 Pair | TS-Q-06 | 17-MC-DCS-002 | 10-FSH-08007 | Pr.01 | 1 | 02 Core | 2 | C.03 | 3 | 4 |  | AI-NIS (4-20 mA, 2 wire) DCS | AVK 2,5 A, AVK 2,5 A | O1010001 | 2 | BP011 | 17-MC-DCS-006 | O1010000 | 1 | 136
O1010002 | 3 | 17-SC-DCS-001 | O1010002 | 16 | AI-NIS (4-20 mA, 2 wire) DCS | AI713-H11 | 10-FSH-08008 | 01 Pair | TS-Q-07 | 17-MC-DCS-002 | 10-FSH-08008 | Pr.01 | 1 | 02 Pair | 4 | C.05 | 5 | 6 |  | AI-NIS (4-20 mA, 4 wire) DCS | AVK 2,5 A, AVK 2,5 A | O1010002 | 3 | BP011 | 17-MC-DCS-006 | O1010001 | 2 | 136
O1010003 | 4 | 17-SC-DCS-001 | O1010003 | 16 | AI-NIS (4-20 mA, 4 wire) DCS | AI713-H11 | 10-FSH-08013 | 01 Pair | TS-Q-08 | 17-MC-DCS-002 | 10-FSH-08013 | Pr.01 | 1 | 05 Pair | 10 | C.07 | 7 | 8 |  | AI-R-IS (4-20 mA, 2 wire) DCS | AVK 2,5 A, AVK 2,5 A | O1010003 | 4 | BP011 | 17-MC-DCS-006 | O1010002 | 3 | 136
O1010004 | 5 | 17-SC-DCS-001 | O1010004 | 16 | AI-R-IS (4-20 mA, 2 wire) DCS | AI713-H11 | 10-FSH-08015 | 01 Pair | TS-Q-09 | 17-MC-DCS-002 | 10-FSH-08015 | Pr.01 | 1 | 06 Pair | 12 | C.09 | 9 | 10 |  | AI-R-IS (4-20 mA, 4 wire) DCS | AVK 2,5 A, AVK 2,5 A | O1010004 | 5 | BP011 | 17-MC-DCS-006 | O1010003 | 4 | 136
O1010005 | 6 | 17-SC-DCS-001 | O1010005 | 16 | AI-R-IS (4-20 mA, 4 wire) DCS | AI713-H11 | 10-FSH-08016 | 01 Pair | TS-Q-10 | 17-MC-DCS-002 | 10-FSH-08016 | Pr.01 | 1 |  | 12 | C.11 | 11 | 12 |  | AI-R-NIS (4-20 mA, 2 wire) DCS | AVK 2,5 A, AVK 2,5 A | O1010005 | 6 | BP011 | 17-MC-DCS-006 | O1010004 | 5 | 136
O1010006 | 7 | 17-SC-DCS-001 | O1010006 | 16 | AI-R-NIS | AI713-H11 | 10-FSH-08017 | 01 Pair | TS-Q-11 | 17-MC-DCS-002 | 10-FSH-08017 | Pr.01 | 1 | 06 Triad | 18 | C.13 | 13 | 14 |  | AI-R-NIS (4-20 mA, 4 wire) DCS | AVK 2,5 A, AVK 2,5 A | O1010006 | 7 | BP011 | 17-MC-DCS-006 | O1010005 | 6 | 136
O1010007 | 8 | 17-SC-DCS-001 | O1010007 | 16 | AI-R-NIS (4-20 mA, 2 wire) DCS | AI713-H11 | 10-FSH-08019 | 01 Pair | TS-Q-12 | 17-MC-DCS-002 | 10-FSH-08019 | Pr.01 | 1 | 08 Core | 8 | C.15 | 15 | 16 |  | AI-RTD-NIS (3 wire) DCS | AVK 2,5 A, AVK 2,5 A, AVK 2,5 A | O1010007 | 8 | BP011 | 17-MC-DCS-006 | O1010006 | 7 | 136
O1010008 | 9 | 17-SC-DCS-001 | O1010008 | 16 | AI-R-NIS (4-20 mA, 4 wire) DCS | AI713-H11 | 11-C-DD-N-001FL10 | 06 Pair | TS-O-10 | 17-MC-DCS-002 | 11-C-DD-N-001FL10 | Pr.01 | 1 | 10 Pair | 20 | C.17 | 17 | 18 |  | AO-NIS (4-20 mA) DCS | AVK 2,5 A, AVK 2,5 A | O1010008 | 9 | BP011 | 17-MC-DCS-006 | O1010007 | 8 | 136
O1010009 | 10 | 17-SC-DCS-001 | O1010009 | 16 | AI-RTD-NIS (3 wire) DCS | AI713-H11 | 11-C-DD-N-001FL20 | 24 Pair | TS-Q-14 | 17-MC-DCS-002 |  | Pr.02 | 1 | 12 Pair | 24 | C.19 | 19 | 20 |  | AO-R-IS (4-20 mA) DCS | AVK 2,5 A, AVK 2,5 A | O1010009 | 10 | BP011 | 17-MC-DCS-008 | O1010008 | 9 | 136
O1010010 | 11 | 17-SC-DCS-001 | O1010010 | 16 | AO-NIS | AO713-H11 | 11-C-DD-N-001FL30 | 12 Pair | TS-O-09 | 17-MC-DCS-002 | 11-C-DD-N-001FL20 | Pr.01 | 1 | 15 Pair | 30 | C.21 | 21 | 22 |  | AO-R-NIS (4-20 mA) DCS | AVK 2,5 A, AVK 2,5 A | O1010010 | 11 | BP011 | 17-MC-DCS-008 | O1010009 | 10 | 136
O1010011 | 12 | 17-SC-DCS-001 | O1010011 | 16 | AO-NIS (4-20 mA) DCS | AO713-H11 | 11-C-DD-N-001FL40 | 06 Pair | TS-P-07 | 17-MC-DCS-002 |  | Pr.02 | 1 | 16 Core | 16 | C.23 | 23 | 24 |  | DI-IS (NAMUR) DCS | AVK 2,5 A, AVK 2,5 A | O1010011 | 12 | BP011 | 17-MC-DCS-009 | O1010010 | 11 | 136
O1010012R | 13 | 17-SC-DCS-001 | O1010012R | 16 | AO-R-IS | AO713-H11 | 11-C-DD-N-002FL50 | 06 Pair | TS-P-08 | 17-MC-DCS-002 | 11-C-DD-N-001FL30 | Pr.01 | 1 | 20 Core | 20 | C.25 | 25 | 26 |  | DI-NIS (Conductivity) DCS | AVK 2,5 A, AVK 2,5 A | O1010012R | 13 | BP011 | 17-MC-DCS-006 | O1010011 | 12 | 136
O1010014R | 15 | 17-SC-DCS-001 | O1010014R | 16 | AO-R-IS (4-20 mA) DCS | AO713-H11 | 17-B-AD-N-001BL02 | 24 Pair | TS-Q-01 | 17-MC-DCS-006 | 11-C-DD-N-001FL40 | Pr.01 | 1 | 24 Pair | 48 | C.27 | 27 | 28 |  | DI-NIS (Diagnostic) DCS | AVK 2,5 A, AVK 2,5 A | O1010014R | 15 | BP011 | 17-MC-DCS-006 | O1010012R | 13 | 136
O1010100R | 1 | 17-SC-DCS-001 | O1010100R | 16 | AO-R-NIS | AO713-H11 | 17-B-AD-N-002BL02 | 06 Pair | TS-O-06 | 17-MC-DCS-006 | 11-C-DD-N-002FL50 | Pr.01 | 1 | 30 Core | 30 | Pr.01 | 1 | 2 |  | DI-NIS (NAMUR) DCS | AVK 2,5 A, AVK 2,5 A | O1010100R | 1 | BP012 | 17-MC-DCS-008 | O1010014R | 15 | 136
O1010102R | 3 | 17-SC-DCS-001 | O1010102R | 16 | AO-R-NIS (4-20 mA) DCS | AO713-H11 | 17-C-AD-I-001FL10 | 12 Pair | TS-G-01 | 17-MC-DCS-009 | 17-B-AD-N-001BL02 | Pr.01 | 1 | (пусто) |  | Pr.02 | 3 | 4 |  | DI-NIS (Thermistors PTC) DCS | AVK 2,5 A, AVK 2,5 A | O1010102R | 3 | BP012 | 17-MC-DCS-009 | O1010100R | 1 | 136
O1010104R | 5 | 17-SC-DCS-001 | O1010104R | 16 | DI-IS | DI715-S11 | 17-C-AD-I-001FL11 | 24 Pair | TS-H-03 | 17-MC-DCS-009 |  | Pr.02 | 1 |  | (пусто) | Pr.03 | 5 | 6 |  | DI-NIS (VFC) DCS | AVK 2,5 A, AVK 2,5 A | O1010104R | 5 | BP012 | 17-MC-DCS-006 | O1010102R | 3 | 136
O1010106R | 7 | 17-SC-DCS-001 | O1010106R | 16 | DI-IS (NAMUR) DCS | DI715-S11 | 17-C-AD-I-001FL11-L111 | 24 Pair | TS-H-04 | 17-MC-DCS-009 |  | Pr.03 | 1 |  |  | Pr.04 | 7 | 8 |  |  | (пусто) | O1010106R | 7 | BP012 | 17-MC-DCS-006 | O1010104R | 5 | 136
O1010108R | 9 | 17-SC-DCS-001 | O1010108R | 16 | DI-NIS (Conductivity) DCS | DI715-S11 | 17-C-AD-I-002FL11 | 12 Pair | TS-G-02 | 17-MC-DCS-009 |  | Pr.04 | 1 |  |  | Pr.05 | 9 | 10 |  | DO-NIS (24VDC) DCS | AVK 2,5 A, AVK 2,5 A | O1010108R | 9 | BP012 | 17-MC-DCS-008 | O1010106R | 7 | 136
O1010110R | 11 | 17-SC-DCS-001 | O1010110R | 16 | DI-NIS (Diagnostic) DCS | DI715-S11 | 17-C-AD-I-003FL11 | 12 Pair | TS-G-03 | 17-MC-DCS-009 |  | Pr.05 | 1 |  |  | Pr.06 | 11 | 12 |  | DO-NIS (VFC NO) DCS | AVK 2,5 A, AVK 2,5 A | O1010110R | 11 | BP012 | 17-MC-DCS-009 | O1010108R | 9 | 136
O1010112R | 13 | 17-SC-DCS-001 | O1010112R | 16 | DI-NIS (NAMUR) DCS | DI715-S11 | 17-C-AD-I-004FL10-L091 | 12 Pair | TS-G-04 | 17-MC-DCS-009 |  | Pr.06 | 1 |  |  | Pr.07 | 13 | 14 |  | PI-R-NIS (Pulse Input) DCS | AVK 2,5 A, AVK 2,5 A | O1010112R | 13 | BP012 | 17-MC-DCS-009 | O1010110R | 11 | 136
O1010114 | 15 | 17-SC-DCS-001 | O1010114 | 16 | DI-NIS (Thermistors PTC) DCS | DI715-S11 | 17-C-AD-N-001FL03-L022 | 24 Pair | TS-O-01 | 17-MC-DCS-008 |  | Pr.07 | 1 |  |  | Pr.08 | 15 | 16 |  | Питание | AVK 2,5 A, AVK 2,5 A | O1010114 | 15 | BP012 | 17-MC-DCS-006 | O1010112R | 13 | 136
O1010115 | 16 | 17-SC-DCS-001 | O1010115 | 32 | DI-NIS (VFC) DCS | DI715-S11 | 17-C-AD-N-001FL07 | 12 Pair | TS-O-01 | 17-MC-DCS-006 |  | Pr.08 | 1 |  |  | Pr.09 | 17 | 18 |  | DI-NIS (MCC) DCS 230 VAC | ASK 3MLD, ASK 3MB | O1010115 | 16 | BP012 | 17-MC-DCS-005 | O1010114 | 15 | 136
O1010200 | 1 | 17-SC-DCS-001 | O1010200 | 32 | DO-NIS (24VDC) DCS | DO716-S11 | 17-C-AD-N-001FL07-L073 | 12 Pair | TS-Q-02 | 17-MC-DCS-006 |  | Pr.09 | 1 |  |  | Pr.10 | 19 | 20 |  | DI-NIS (MCC) DCS 220 VDC | ASK 3MLD, ASK 3MB | O1010200 | 1 | BP021 | 17-MC-DCS-001 | O1010115 | 16 | 528
O1010201 | 2 | 17-SC-DCS-001 | O1010201 | 32 | DO-NIS (VFC NO) DCS | DO716-S11 | 17-C-AD-N-001FL10 | 24 Pair | TS-O-02 | 17-MC-DCS-006 |  | Pr.10 | 1 |  |  | Pr.11 | 21 | 22 |  |  | (пусто) | O1010201 | 2 | BP021 | 17-MC-DCS-001 | O1010200 | 1 | 528
O1010202 | 3 | 17-SC-DCS-001 | O1010202 | 32 | PI-R-NIS (Pulse Input) DCS | AI713-H11 | 17-C-AD-N-001FL10-K101 | 24 Pair | TS-O-03 | 17-MC-DCS-006 |  | Pr.11 | 1 |  |  | Pr.12 | 23 | 24 |  | DI-NIS | (пусто) | O1010202 | 3 | BP021 | 17-MC-DCS-001 | O1010201 | 2 | 528
O1010203 | 4 | 17-SC-DCS-001 | O1010203 | 32 | Питание | (пусто) | 17-C-AD-N-001FL11 | 12 Pair | TS-O-04 | 17-MC-DCS-006 |  | Pr.12 | 1 |  |  | Pr.13 | 25 | 26 |  | DO-NIS (MCC) DCS 230 VAC | ASK 3MLD, ASK 3MB | O1010203 | 4 | BP021 | 17-MC-DCS-001 | O1010202 | 3 | 528
O1010204 | 5 | 17-SC-DCS-001 | O1010204 | 32 | DI-NIS (MCC) DCS 230 VAC | DI715-S11 | 17-C-AD-N-001FL11-AH001 | 12 Pair | TS-R-05 | 17-MC-DCS-006 |  | Pr.13 | 1 |  |  | Pr.14 | 27 | 28 |  | DO-NIS (MCC) DCS 220 VDC | ASK 3MLD, ASK 3MB | O1010204 | 5 | BP021 | 17-MC-DCS-002 | O1010203 | 4 | 528
O1010205 | 6 | 17-SC-DCS-001 | O1010205 | 32 | DI-NIS (MCC) DCS 220 VDC | DI715-S11 | 17-C-AD-N-001FL11-L111 | 24 Pair | TS-O-05 | 17-MC-DCS-006 |  | Pr.14 | 1 |  |  | Pr.15 | 29 | 30 |  |  |  | O1010205 | 6 | BP021 | 17-MC-DCS-004 | O1010204 | 5 | 528
O1010206 | 7 | 17-SC-DCS-001 | O1010206 | 32 | DI-NIS | DI715-S11 | 17-C-AD-N-001FL11-L112 | 12 Pair | TS-R-01 | 17-MC-DCS-006 |  | Pr.15 | 1 |  |  | Pr.16 | 31 | 32 |  |  |  | O1010206 | 7 | BP021 | 17-MC-DCS-003 | O1010205 | 6 | 528
O1010207 | 8 | 17-SC-DCS-001 | O1010207 | 32 | DO-NIS (MCC) DCS 230 VAC | DO716-S11 | 17-C-AD-N-001FL17 | 24 Pair | TS-O-02 | 17-MC-DCS-008 |  | Pr.16 | 1 |  |  | Pr.17 | 33 | 34 |  |  |  | O1010207 | 8 | BP021 | 17-MC-DCS-003 | O1010206 | 7 | 528
O1010208 | 9 | 17-SC-DCS-001 | O1010208 | 32 | DO-NIS (MCC) DCS 220 VDC | DO716-S11 | 17-C-AD-N-001-LP003-L111 | 12 Pair | TS-Q-08 | 17-MC-DCS-006 | 17-B-AD-N-002BL02 | Pr.01 | 1 |  |  | Pr.18 | 35 | 36 |  |  |  | O1010208 | 9 | BP021 | 17-MC-DCS-003 | O1010207 | 8 | 528
O1010209 | 10 | 17-SC-DCS-001 | O1010209 | 32 | AI-NIS | AI713-H11 | 17-C-AD-N-002FL03-L022 | 24 Pair | TS-O-03 | 17-MC-DCS-008 |  | Pr.02 | 1 |  |  | Pr.19 | 37 | 38 |  |  |  | O1010209 | 10 | BP021 | 17-MC-DCS-005 | O1010208 | 9 | 528
O1010210 | 11 | 17-SC-DCS-001 | O1010210 | 32 | AI-R-IS | AI713-H11 | 17-C-AD-N-002FL07 | 24 Pair | TS-Q-03 | 17-MC-DCS-006 |  | Pr.03 | 1 |  |  | Pr.20 | 39 | 40 |  |  |  | O1010210 | 11 | BP021 | 17-MC-DCS-001 | O1010209 | 10 | 528
O1010211 | 12 | 17-SC-DCS-001 | O1010211 | 32 |  |  | 17-C-AD-N-002FL07-L073 | 06 Pair | TS-O-04 | 17-MC-DCS-008 |  | Pr.04 | 1 |  |  | Pr.21 | 41 | 42 |  |  |  | O1010211 | 12 | BP021 | 17-MC-DCS-001 | O1010210 | 11 | 528
O1010212 | 13 | 17-SC-DCS-001 | O1010212 | 32 |  |  | 17-C-AD-N-002FL10 | 24 Pair | TS-P-01 | 17-MC-DCS-008 |  | Pr.05 | 1 |  |  | Pr.22 | 43 | 44 |  |  |  | O1010212 | 13 | BP021 | 17-MC-DCS-003 | O1010211 | 12 | 528
O1010213 | 14 | 17-SC-DCS-001 | O1010213 | 32 |  |  | 17-C-AD-N-002FL11-L111 | 24 Pair | TS-P-02 | 17-MC-DCS-008 | 17-C-AD-I-001FL10 | Pr.01 | 1 |  |  | Pr.23 | 45 | 46 |  |  |  | O1010213 | 14 | BP021 | 17-MC-DCS-003 | O1010212 | 13 | 528
O1010214 | 15 | 17-SC-DCS-001 | O1010214 | 32 |  |  | 17-C-AD-N-002FL14 | 12 Pair | TS-O-05 | 17-MC-DCS-008 |  | Pr.02 | 1 |  |  | Tr.01 | 1 | 2 | 3 |  |  | O1010214 | 15 | BP021 | 17-MC-DCS-003 | O1010213 | 14 | 528
O1010215 | 16 | 17-SC-DCS-001 | O1010215 | 32 |  |  | 17-C-AD-N-003FL03-L022 | 12 Pair | TS-O-06 | 17-MC-DCS-008 |  | Pr.03 | 1 |  |  | Tr.02 | 4 | 5 | 6 |  |  | O1010215 | 16 | BP021 | 17-MC-DCS-005 | O1010214 | 15 | 528
O1010300 | 1 | 17-SC-DCS-001 | O1010300 | 32 |  |  | 17-C-AD-N-003FL07-L073 | 06 Pair | TS-O-07 | 17-MC-DCS-008 |  | Pr.04 | 1 |  |  | Tr.03 | 7 | 8 | 9 |  |  | O1010300 | 1 | BP022 | 17-MC-DCS-005 | O1010215 | 16 | 528
O1010301 | 2 | 17-SC-DCS-001 | O1010301 | 32 |  |  | 17-C-AD-N-003FL10 | 24 Pair | TS-Q-04 | 17-MC-DCS-006 |  | Pr.05 | 1 |  |  | Tr.04 | 10 | 11 | 12 |  |  | O1010301 | 2 | BP022 | 17-MC-DCS-004 | O1010300 | 1 | 528
O1011000 | 1 | 17-SC-DCS-002 | O1011000 | 16 |  |  | 17-C-AD-N-003FL11-L111 | 12 Pair | TS-P-04 | 17-MC-DCS-008 |  | Pr.06 | 1 |  |  | Tr.05 | 13 | 14 | 15 |  |  | O1011000 | 1 | BP011 | 17-MC-DCS-006 | O1010301 | 2 | 528
O1011001 | 2 | 17-SC-DCS-002 | O1011001 | 16 |  |  | 17-C-AD-N-004FL07-L073 | 06 Pair | TS-O-08 | 17-MC-DCS-008 |  | Pr.07 | 1 |  |  | (пусто) | (пусто) | (пусто) |  |  |  | O1011001 | 2 | BP011 | 17-MC-DCS-008 | O1011000 | 1 | 136
O1011002 | 3 | 17-SC-DCS-002 | O1011002 | 16 |  |  | 17-C-AD-N-004FL10 | 24 Pair | TS-Q-05 | 17-MC-DCS-006 |  | Pr.08 | 1 | [8 empty] | O1011002 | 3 | BP011 | 17-MC-DCS-008 | O1011001 | 2 | 136
O1011003 | 4 | 17-SC-DCS-002 | O1011003 | 16 |  |  | 17-C-AD-N-005FL03-L022 | 06 Pair | TS-O-09 | 17-MC-DCS-008 | 17-C-AD-I-001FL11 | Pr.01 | 1 | [8 empty] | O1011003 | 4 | BP011 | 17-MC-DCS-008 | O1011002 | 3 | 136
O1011004 | 5 | 17-SC-DCS-002 | O1011004 | 16 |  |  | 17-C-AD-N-005FL07-L073 | 06 Pair | TS-R-02 | 17-MC-DCS-006 |  | Pr.02 | 1 | [8 empty] | O1011004 | 5 | BP011 | 17-MC-DCS-008 | O1011003 | 4 | 136
O1011005 | 6 | 17-SC-DCS-002 | O1011005 | 16 |  |  | 17-C-AD-N-006FL03-L022 | 24 Pair | TS-P-03 | 17-MC-DCS-008 |  | Pr.03 | 1 | [8 empty] | O1011005 | 6 | BP011 | 17-MC-DCS-009 | O1011004 | 5 | 136
O1011006 | 7 | 17-SC-DCS-002 | O1011006 | 16 |  |  | 17-C-AD-N-702FL11-L111 | 06 Pair | TS-Q-06 | 17-MC-DCS-006 |  | Pr.04 | 1 | [8 empty] | O1011006 | 7 | BP011 | 17-MC-DCS-009 | O1011005 | 6 | 136
O1011008R | 9 | 17-SC-DCS-002 | O1011008R | 16 |  |  | 17-C-AP-I-002FL10-L091 | 06 Pair | TS-H-01 | 17-MC-DCS-009 |  | Pr.06 | 1 | [8 empty] | O1011008R | 9 | BP011 | 17-MC-DCS-007 | O1011006 | 7 | 136
O1011010R | 11 | 17-SC-DCS-002 | O1011010R | 16 |  |  | 17-C-CD-N-001FL03-L022 | 30 Core | TS-O-01 | 17-MC-DCS-002 |  | Pr.07 | 1 | [8 empty] | O1011010R | 11 | BP011 | 17-MC-DCS-008 | O1011008R | 9 | 136
O1011012R | 13 | 17-SC-DCS-002 | O1011012R | 16 |  |  | 17-C-CD-N-001FL07 | 30 Core | TS-G-01 | 17-MC-DCS-001 |  | Pr.08 | 1 | [8 empty] | O1011012R | 13 | BP011 | 17-MC-DCS-006 | O1011010R | 11 | 136
O1011014R | 15 | 17-SC-DCS-002 | O1011014R | 16 |  |  | 17-C-CD-N-001FL07-L073 | 30 Core | TS-O-02 | 17-MC-DCS-002 |  | Pr.09 | 1 | [8 empty] | O1011014R | 15 | BP011 | 17-MC-DCS-008 | O1011012R | 13 | 136
O1011100 | 1 | 17-SC-DCS-002 | O1011100 | 32 |  |  | 17-C-CD-N-001FL10 | 16 Core | TS-G-02 | 17-MC-DCS-001 |  | Pr.10 | 1 | [8 empty] | O1011100 | 1 | BP012 | 17-MC-DCS-002 | O1011014R | 15 | 136
O1011101 | 2 | 17-SC-DCS-002 | O1011101 | 32 |  |  | 17-C-CD-N-002FL03-L022 | 16 Core | TS-O-03 | 17-MC-DCS-002 |  | Pr.11 | 1 | [8 empty] | O1011101 | 2 | BP012 | 17-MC-DCS-002 | O1011100 | 1 | 528
O1011102 | 3 | 17-SC-DCS-002 | O1011102 | 32 |  |  | 17-C-CD-N-002FL07 | 30 Core | TS-G-03 | 17-MC-DCS-001 |  | Pr.12 | 1 | [8 empty] | O1011102 | 3 | BP012 | 17-MC-DCS-002 | O1011101 | 2 | 528
O1011103 | 4 | 17-SC-DCS-002 | O1011103 | 32 |  |  | 17-C-CD-N-002FL10 | 30 Core | TS-G-04 | 17-MC-DCS-001 |  | Pr.14 | 1 | [8 empty] | O1011103 | 4 | BP012 | 17-MC-DCS-002 | O1011102 | 3 | 528
O1011104 | 5 | 17-SC-DCS-002 | O1011104 | 32 |  |  | 17-C-CD-N-003FL03-L022 | 16 Core | TS-O-04 | 17-MC-DCS-002 |  | Pr.16 | 1 | [8 empty] | O1011104 | 5 | BP012 | 17-MC-DCS-002 | O1011103 | 4 | 528
O1011105 | 6 | 17-SC-DCS-002 | O1011105 | 32 |  |  | 17-C-CD-N-003FL07 | 30 Core | TS-G-05 | 17-MC-DCS-001 |  | Pr.17 | 1 | [8 empty] | O1011105 | 6 | BP012 | 17-MC-DCS-002 | O1011104 | 5 | 528
O1011106 | 7 | 17-SC-DCS-002 | O1011106 | 32 |  |  | 17-C-CD-N-004FL03-L022 | 30 Core | TS-O-05 | 17-MC-DCS-002 |  | Pr.19 | 1 | [8 empty] | O1011106 | 7 | BP012 | 17-MC-DCS-004 | O1011105 | 6 | 528
O1011107 | 8 | 17-SC-DCS-002 | O1011107 | 32 |  |  | 17-C-CD-N-005FL03-L022 | 30 Core | TS-O-06 | 17-MC-DCS-002 | 17-C-AD-I-001FL11-L111 | Pr.04 | 1 | [8 empty] | O1011107 | 8 | BP012 | 17-MC-DCS-004 | O1011106 | 7 | 528
O1011108 | 9 | 17-SC-DCS-002 | O1011108 | 32 |  |  | 17-C-CD-N-006FL03-L022 | 30 Core | TS-P-01 | 17-MC-DCS-002 |  | Pr.05 | 1 | [8 empty] | O1011108 | 9 | BP012 | 17-MC-DCS-004 | O1011107 | 8 | 528
O1011109 | 10 | 17-SC-DCS-002 | O1011109 | 32 |  |  | 17-C-CD-N-006FL10-L091 | 30 Core | TS-P-02 | 17-MC-DCS-002 |  | Pr.06 | 1 | [8 empty] | O1011109 | 10 | BP012 | 17-MC-DCS-004 | O1011108 | 9 | 528
O1011110 | 11 | 17-SC-DCS-002 | O1011110 | 32 |  |  | 17-C-CD-N-007FL03-L022 | 30 Core | TS-P-03 | 17-MC-DCS-002 |  | Pr.07 | 1 | [8 empty] | O1011110 | 11 | BP012 | 17-MC-DCS-004 | O1011109 | 10 | 528
O1011111 | 12 | 17-SC-DCS-002 | O1011111 | 32 |  |  | 17-C-CD-N-009FL03-L022 | 30 Core | TS-H-05 | 17-MC-DCS-001 |  | Pr.08 | 1 | [8 empty] | O1011111 | 12 | BP012 | 17-MC-DCS-005 | O1011110 | 11 | 528
O1011112 | 13 | 17-SC-DCS-002 | O1011112 | 32 |  |  | 17-C-CD-N-010FL03-L022 | 30 Core | TS-P-04 | 17-MC-DCS-002 |  | Pr.09 | 1 | [8 empty] | O1011112 | 13 | BP012 | 17-MC-DCS-005 | O1011111 | 12 | 528
O1011113 | 14 | 17-SC-DCS-002 | O1011113 | 32 |  |  | 17-C-DB-N-001FL11-L111 | 24 Pair | TS-F-01 | 17-MC-DCS-001 |  | Pr.10 | 1 | [8 empty] | O1011113 | 14 | BP012 | 17-MC-DCS-007 | O1011112 | 13 | 528
O1011114 | 15 | 17-SC-DCS-002 | O1011114 | 32 |  |  | 17-C-DD-001-LP001-K101 | 12 Pair | TS-F-01 | 17-MC-DCS-007 |  | Pr.11 | 1 | [8 empty] | O1011114 | 15 | BP012 | 17-MC-DCS-007 | O1011113 | 14 | 528
O1011115 | 16 | 17-SC-DCS-002 | O1011200 | 32 |  |  | 17-C-DD-002-LP001-K101 | 30 Core | TS-G-01 | 17-MC-DCS-007 |  | Pr.12 | 1 | [8 empty] | O1011115 | 16 | BP012 | 17-MC-DCS-009 | O1011114 | 15 | 528
O1011200 | 1 | 17-SC-DCS-002 | O1011115 | 32 |  |  | 17-C-DD-I-005FL10-L091 | 24 Pair | TS-G-05 | 17-MC-DCS-009 | 17-C-AD-I-002FL11 | Pr.01 | 1 | [8 empty] | O1011200 | 1 | BP021 | 17-MC-DCS-007 | O1011200 | 1 | 528
O1011201 | 2 | 17-SC-DCS-002 | O1011201 | 32 |  |  | 17-C-DD-N-001FL03-L022 | 12 Pair | TS-O-07 | 17-MC-DCS-002 |  | Pr.02 | 1 | [8 empty] | O1011201 | 2 | BP021 | 17-MC-DCS-007 | O1011115 | 16 | 528
O1011202 | 3 | 17-SC-DCS-002 | O1011202 | 32 |  |  | 17-C-DD-N-001FL07 | 24 Pair | TS-F-02 | 17-MC-DCS-001 |  | Pr.03 | 1 | [8 empty] | O1011202 | 3 | BP021 | 17-MC-DCS-002 | O1011201 | 2 | 528
O1011203 | 4 | 17-SC-DCS-002 | O1011203 | 32 |  |  | 17-C-DD-N-001FL10 | 06 Pair | TS-F-03 | 17-MC-DCS-001 |  | Pr.04 | 1 | [8 empty] | O1011203 | 4 | BP021 | 17-MC-DCS-002 | O1011202 | 3 | 528
O1011204 | 5 | 17-SC-DCS-002 | O1011204 | 32 |  |  | 17-C-DD-N-001FL11-AH001 | 06 Pair | TS-F-18 | 17-MC-DCS-007 |  | Pr.05 | 1 | [8 empty] | O1011204 | 5 | BP021 | 17-MC-DCS-002 | O1011203 | 4 | 528
O1011205 | 6 | 17-SC-DCS-002 | O1011205 | 32 |  |  | 17-C-DD-N-001FL11-L111 | 06 Pair | TS-G-06 | 17-MC-DCS-001 |  | Pr.06 | 1 | [8 empty] | O1011205 | 6 | BP021 | 17-MC-DCS-004 | O1011204 | 5 | 528
O1011206 | 7 | 17-SC-DCS-002 | O1011206 | 32 |  |  | 17-C-DD-N-001FL14 | 24 Pair | TS-O-08 | 17-MC-DCS-002 |  | Pr.07 | 1 | [8 empty] | O1011206 | 7 | BP021 | 17-MC-DCS-004 | O1011205 | 6 | 528
O1011207 | 8 | 17-SC-DCS-002 | O1011207 | 32 |  |  | 17-C-DD-N-001-LP001-P111A | 06 Pair | TS-F-15 | 17-MC-DCS-007 |  | Pr.08 | 1 | [8 empty] | O1011207 | 8 | BP021 | 17-MC-DCS-004 | O1011206 | 7 | 528
O1011208 | 9 | 17-SC-DCS-002 | O1011208 | 32 |  |  | 17-C-DD-N-001-LP002-L111 | 12 Pair | TS-F-02 | 17-MC-DCS-007 |  | Pr.09 | 1 | [8 empty] | O1011208 | 9 | BP021 | 17-MC-DCS-004 | O1011207 | 8 | 528
O1011209 | 10 | 17-SC-DCS-002 | O1011209 | 32 |  |  | 17-C-DD-N-001-LP003A-L091 | 06 Pair | TS-F-03 | 17-MC-DCS-007 | 17-C-AD-I-003FL11 | Pr.01 | 1 | [8 empty] | O1011209 | 10 | BP021 | 17-MC-DCS-005 | O1011208 | 9 | 528
O1011210 | 11 | 17-SC-DCS-002 | O1011210 | 32 |  |  | 17-C-DD-N-001-LP003B-L091 | 06 Pair | TS-F-04 | 17-MC-DCS-007 |  | Pr.02 | 1 | [8 empty] | O1011210 | 11 | BP021 | 17-MC-DCS-007 | O1011209 | 10 | 528
O1011211 | 12 | 17-SC-DCS-002 | O1011211 | 32 |  |  | 17-C-DD-N-001-LP003-L111 | 12 Pair | TS-F-04 | 17-MC-DCS-001 |  | Pr.03 | 1 | [8 empty] | O1011211 | 12 | BP021 | 17-MC-DCS-007 | O1011210 | 11 | 528
O1011212 | 13 | 17-SC-DCS-002 | O1011212 | 32 |  |  | 17-C-DD-N-002FL03-L022 | 12 Pair | TS-R-01 | 17-MC-DCS-002 |  | Pr.04 | 1 | [8 empty] | O1011212 | 13 | BP021 | 17-MC-DCS-001 | O1011211 | 12 | 528
O1011213 | 14 | 17-SC-DCS-002 | O1011213 | 32 |  |  | 17-C-DD-N-002FL07 | 24 Pair | TS-F-05 | 17-MC-DCS-001 |  | Pr.05 | 1 | [8 empty] | O1011213 | 14 | BP021 | 17-MC-DCS-003 | O1011212 | 13 | 528
O1011300R | 1 | 17-SC-DCS-002 | O1011300R | 16 |  |  | 17-C-DD-N-002FL10 | 24 Pair | TS-F-06 | 17-MC-DCS-001 |  | Pr.06 | 1 | [8 empty] | O1011300R | 1 | BP022 | 17-MC-DCS-009 | O1011213 | 14 | 528
O1011302R | 3 | 17-SC-DCS-002 | O1011302R | 16 |  |  | 17-C-DD-N-002FL11-L111 | 24 Pair | TS-H-02 | 17-MC-DCS-001 | 17-C-AD-I-004FL10-L091 | Pr.01 | 1 | [8 empty] | O1011302R | 3 | BP022 | 17-MC-DCS-008 | O1011300R | 1 | 136
O1011304 | 5 | 17-SC-DCS-002 | O1011304 | 32 |  |  | 17-C-DD-N-002FL11-L111-CD | 30 Core | TS-G-07 | 17-MC-DCS-001 |  | Pr.02 | 1 | [8 empty] | O1011304 | 5 | BP022 | 17-MC-DCS-005 | O1011302R | 3 | 136
(пусто) | (пусто) | (пусто) |  |  |  |  | 17-C-DD-N-002-LP001-P111A | 02 Core | TS-H-02 | 17-MC-DCS-007 |  | Pr.03 | 1 | [8 empty] | (пусто) | (пусто) | (пусто) | 17-MC-DCS-008 | O1011304 | 5 | 528
[7 empty] | 17-C-DD-N-002-LP002-L111 | 08 Core | TS-G-02 | 17-MC-DCS-007 |  | Pr.04 | 1
[7 empty] | 17-C-DD-N-002-LP003A-L091 | 16 Core | TS-G-03 | 17-MC-DCS-007 |  | Pr.05 | 1
[7 empty] | 17-C-DD-N-002-LP003B-L091 | 02 Core | TS-H-01 | 17-MC-DCS-007 |  | Pr.06 | 1
[7 empty] | 17-C-DD-N-003FL03-L022 | 12 Pair | TS-R-02 | 17-MC-DCS-002 | 17-C-AD-N-001FL03-L022 | Pr.01 | 1
[7 empty] | 17-C-DD-N-003FL07 | 24 Pair | TS-R-03 | 17-MC-DCS-002 |  | Pr.02 | 1
[7 empty] | 17-C-DD-N-003FL10 | 12 Pair | TS-Q-02 | 17-MC-DCS-004 |  | Pr.03 | 1
[7 empty] | 17-C-DD-N-003FL11-L111 | 24 Pair | TS-H-01 | 17-MC-DCS-001 |  | Pr.04 | 1
[7 empty] | 17-C-DD-N-003-LP001-P111A | 02 Core | TS-H-03 | 17-MC-DCS-007 |  | Pr.05 | 1
[7 empty] | 17-C-DD-N-004FL03-L022 | 24 Pair | TS-R-04 | 17-MC-DCS-002 |  | Pr.06 | 1
[7 empty] | 17-C-DD-N-004FL10 | 12 Pair | TS-G-08 | 17-MC-DCS-001 |  | Pr.07 | 1
[7 empty] | 17-C-DD-N-005FL03-L022 | 24 Pair | TS-P-05 | 17-MC-DCS-002 |  | Pr.08 | 1
[7 empty] | 17-C-DD-N-006FL03-L022 | 24 Pair | TS-Q-01 | 17-MC-DCS-002 |  | Pr.09 | 1
[7 empty] | 17-C-DD-N-007FL03-L022 | 24 Pair | TS-Q-02 | 17-MC-DCS-002 |  | Pr.10 | 1
[7 empty] | 17-C-DD-N-009FL03-L022 | 24 Pair | TS-Q-03 | 17-MC-DCS-002 |  | Pr.11 | 1
[7 empty] | 17-C-DD-N-010FL03-L022 | 12 Pair | TS-Q-04 | 17-MC-DCS-002 |  | Pr.12 | 1
[7 empty] | 17-C-DD-N-1-FL50 | 10 Pair | TS-H-03 | 17-MC-DCS-001 |  | Pr.13 | 1
[7 empty] | 17-C-RD-N-002FL10-K101 | 06 Triad | TS-Q-07 | 17-MC-DCS-006 |  | Pr.14 | 1
[7 empty] | 17-C-XD-N-707FL11-L111 | 06 Triad | TS-F-16 | 17-MC-DCS-007 |  | Pr.15 | 1
[7 empty] | 17-C-СD-N-1-FL50 | 20 Core | TS-H-04 | 17-MC-DCS-001 |  | Pr.16 | 1
[7 empty] | 17-FSL -11101 | 01 Pair | TS-G-08 | 17-MC-DCS-009 |  | Pr.17 | 1
[7 empty] | 17-FSL-17101-CV | 01 Pair | TS-H-08 | 17-MC-DCS-007 | 17-C-AD-N-001FL07 | Pr.02 | 1
[7 empty] | 17-I-AD-N-001BL02 | 12 Pair | TS-R-03 | 17-MC-DCS-006 |  | Pr.03 | 1
[7 empty] | 17-I-CD-N-001BL02 | 30 Core | TS-H-01 | 17-MC-DCS-005 |  | Pr.04 | 1
[7 empty] | 17-I-CD-N-002BL02 | 30 Core | TS-H-02 | 17-MC-DCS-005 |  | Pr.05 | 1
[7 empty] | 17-I-CD-N-003BL02 | 30 Core | TS-H-03 | 17-MC-DCS-005 |  | Pr.06 | 1
[7 empty] | 17-I-CD-N-004BL02 | 30 Core | TS-P-01 | 17-MC-DCS-004 |  | Pr.07 | 1
[7 empty] | 17-I-CD-N-005BL02 | 30 Core | TS-G-01 | 17-MC-DCS-003 |  | Pr.08 | 1
[7 empty] | 17-I-CD-N-006BL02 | 30 Core | TS-G-02 | 17-MC-DCS-003 |  | Pr.09 | 1
[7 empty] | 17-I-CD-N-007BL02 | 30 Core | TS-G-03 | 17-MC-DCS-003 | 17-C-AD-N-001FL07-L073 | Pr.01 | 1
[7 empty] | 17-I-CD-N-008BL02 | 30 Core | TS-G-04 | 17-MC-DCS-003 |  | Pr.02 | 1
[7 empty] | 17-I-CD-N-009BL02 | 30 Core | TS-G-05 | 17-MC-DCS-003 |  | Pr.03 | 1
[7 empty] | 17-I-CD-N-010BL02 | 30 Core | TS-G-06 | 17-MC-DCS-003 |  | Pr.04 | 1
[7 empty] | 17-I-CD-N-011BL02 | 30 Core | TS-G-07 | 17-MC-DCS-003 |  | Pr.05 | 1
[7 empty] | 17-I-CD-N-012BL02 | 30 Core | TS-O-01 | 17-MC-DCS-004 |  | Pr.06 | 1
[7 empty] | 17-I-CD-N-013BL02 | 30 Core | TS-O-02 | 17-MC-DCS-004 | 17-C-AD-N-001FL10 | Pr.01 | 1
[7 empty] | 17-I-CD-N-014BL02 | 30 Core | TS-O-03 | 17-MC-DCS-004 |  | Pr.02 | 1
[7 empty] | 17-I-CD-N-015BL02 | 30 Core | TS-O-04 | 17-MC-DCS-004 |  | Pr.03 | 1
[7 empty] | 17-I-CD-N-016BL02 | 30 Core | TS-P-02 | 17-MC-DCS-004 |  | Pr.04 | 1
[7 empty] | 17-I-CD-N-017BL02 | 16 Core | TS-P-07 | 17-MC-DCS-004 |  | Pr.05 | 1
[7 empty] | 17-I-CD-N-018BL02 | 30 Core | TS-G-08 | 17-MC-DCS-003 |  | Pr.06 | 1
[7 empty] | 17-I-CD-N-019BL02 | 30 Core | TS-H-04 | 17-MC-DCS-005 |  | Pr.07 | 1
[7 empty] | 17-I-CD-N-020BL02 | 16 Core | TS-F-01 | 17-MC-DCS-003 |  | Pr.08 | 1
[7 empty] | 17-I-CD-N-021BL02 | 30 Core | TS-P-03 | 17-MC-DCS-004 |  | Pr.09 | 1
[7 empty] | 17-I-CD-N-022BL02 | 30 Core | TS-P-04 | 17-MC-DCS-004 |  | Pr.10 | 1
[7 empty] | 17-I-CD-N-023BL02 | 30 Core | TS-P-05 | 17-MC-DCS-004 |  | Pr.11 | 1
[7 empty] | 17-I-DD-N-001BL02 | 24 Pair | TS-G-01 | 17-MC-DCS-005 |  | Pr.12 | 1
[7 empty] | 17-I-DD-N-001BL02-L091 | 06 Pair | TS-H-06 | 17-MC-DCS-007 |  | Pr.13 | 1
[7 empty] | 17-I-DD-N-001-BL02-L091 | 06 Pair | TS-F-17 | 17-MC-DCS-007 |  | Pr.14 | 1
[7 empty] | 17-I-DD-N-001-BL02-L101 | 30 Core | TS-H-07 | 17-MC-DCS-007 |  | Pr.15 | 1
[7 empty] | 17-I-DD-N-002BL02 | 24 Pair | TS-F-02 | 17-MC-DCS-003 |  | Pr.16 | 1
[7 empty] | 17-I-DD-N-002BL02-L091 | 06 Pair | TS-H-05 | 17-MC-DCS-007 |  | Pr.17 | 1
[7 empty] | 17-I-DD-N-002-BL02-L101 | 06 Pair | TS-H-04 | 17-MC-DCS-007 |  | Pr.18 | 1
[7 empty] | 17-I-DD-N-003BL02 | 24 Pair | TS-F-03 | 17-MC-DCS-003 |  | Pr.19 | 1
[7 empty] | 17-I-DD-N-004BL02 | 24 Pair | TS-F-04 | 17-MC-DCS-003 |  | Pr.20 | 1
[7 empty] | 17-I-DD-N-005BL02 | 24 Pair | TS-F-05 | 17-MC-DCS-003 | 17-C-AD-N-001FL10-K101 | Pr.01 | 1
[7 empty] | 17-I-DD-N-006BL02 | 24 Pair | TS-F-01 | 17-MC-DCS-005 |  | Pr.02 | 1
[7 empty] | 17-I-DD-N-007BL02 | 24 Pair | TS-H-01 | 17-MC-DCS-003 |  | Pr.03 | 1
[7 empty] | 17-I-DD-N-008BL02 | 24 Pair | TS-O-05 | 17-MC-DCS-004 |  | Pr.04 | 1
[7 empty] | 17-I-DD-N-009BL02 | 24 Pair | TS-O-06 | 17-MC-DCS-004 |  | Pr.05 | 1
[7 empty] | 17-I-DD-N-010BL02 | 24 Pair | TS-R-01 | 17-MC-DCS-004 |  | Pr.06 | 1
[7 empty] | 17-I-DD-N-011BL02 | 24 Pair | TS-R-02 | 17-MC-DCS-004 |  | Pr.07 | 1
[7 empty] | 17-I-DD-N-012BL02 | 24 Pair | TS-R-03 | 17-MC-DCS-004 |  | Pr.08 | 1
[7 empty] | 17-I-DD-N-013BL02 | 24 Pair | TS-G-02 | 17-MC-DCS-005 |  | Pr.09 | 1
[7 empty] | 17-I-DD-N-014BL02 | 24 Pair | TS-G-03 | 17-MC-DCS-005 |  | Pr.10 | 1
[7 empty] | 17-I-DD-N-015BL02 | 24 Pair | TS-R-04 | 17-MC-DCS-004 |  | Pr.11 | 1
[7 empty] | 17-I-DD-N-016BL02 | 12 Pair | TS-P-06 | 17-MC-DCS-004 |  | Pr.12 | 1
[7 empty] | 17-I-DD-N-017BL02 | 24 Pair | TS-F-02 | 17-MC-DCS-005 |  | Pr.13 | 1
[7 empty] | 17-I-DD-N-018BL02 | 24 Pair | TS-F-03 | 17-MC-DCS-005 |  | Pr.14 | 1
[7 empty] | 17-I-DD-N-019BL02 | 24 Pair | TS-F-04 | 17-MC-DCS-005 | 17-C-AD-N-001FL11 | Pr.01 | 1
[7 empty] | 17-I-DD-N-020BL02 | 24 Pair | TS-G-04 | 17-MC-DCS-005 |  | Pr.02 | 1
[7 empty] | 17-I-DD-N-021BL02 | 24 Pair | TS-R-05 | 17-MC-DCS-004 |  | Pr.03 | 1
[7 empty] | 17-I-DD-N-022BL02 | 06 Pair | TS-G-04 | 17-MC-DCS-007 |  | Pr.04 | 1
[7 empty] | 17-I-DD-N-023BL02 | 02 Pair | TS-F-05 | 17-MC-DCS-007 |  | Pr.05 | 1
[7 empty] | 17-I-DD-N-024BL02 | 24 Pair | TS-Q-01 | 17-MC-DCS-004 |  | Pr.07 | 1
[7 empty] | 17-I-DD-N-101BL02 | 06 Pair | TS-G-05 | 17-MC-DCS-007 |  | Pr.10 | 1
[7 empty] | 17-I-DD-N-102BL02 | 06 Pair | TS-G-06 | 17-MC-DCS-007 | 17-C-AD-N-001FL11-AH001 | Pr.01 | 1
[7 empty] | 17-I-DD-N-103BL02 | 06 Pair | TS-G-07 | 17-MC-DCS-007 |  | Pr.02 | 1
[7 empty] | 17-I-DD-N-104BL02 | 06 Pair | TS-G-08 | 17-MC-DCS-007 |  | Pr.03 | 1
[7 empty] | 17-I-DD-N-105BL02 | 06 Pair | TS-G-09 | 17-MC-DCS-007 |  | Pr.04 | 1
[7 empty] | 17-I-DD-N-106BL02 | 06 Pair | TS-G-10 | 17-MC-DCS-007 |  | Pr.05 | 1
[7 empty] | 17-I-DD-N-107BL02 | 06 Pair | TS-G-11 | 17-MC-DCS-007 |  | Pr.06 | 1
[7 empty] | 17-I-DD-N-108BL02 | 06 Pair | TS-G-12 | 17-MC-DCS-007 |  | Pr.07 | 1
[7 empty] | 17-I-DD-N-109BL02 | 06 Pair | TS-G-13 | 17-MC-DCS-007 |  | Pr.08 | 1
[7 empty] | 17-I-DD-N-110BL02 | 06 Pair | TS-G-14 | 17-MC-DCS-007 |  | Pr.09 | 1
[7 empty] | 17-I-DD-N-111BL02 | 06 Pair | TS-G-15 | 17-MC-DCS-007 |  | Pr.10 | 1
[7 empty] | 17-I-DD-N-112BL02 | 06 Pair | TS-G-16 | 17-MC-DCS-007 | 17-C-AD-N-001FL11-L111 | Pr.01 | 1
[7 empty] | 17-I-DD-N-113BL02 | 06 Pair | TS-G-17 | 17-MC-DCS-007 |  | Pr.02 | 1
[7 empty] | 17-I-DD-N-114BL02 | 06 Pair | TS-F-06 | 17-MC-DCS-007 |  | Pr.03 | 1
[7 empty] | 17-I-DD-N-115BL02 | 06 Pair | TS-F-07 | 17-MC-DCS-007 |  | Pr.04 | 1
[7 empty] | 17-I-DD-N-116BL02 | 06 Pair | TS-F-08 | 17-MC-DCS-007 |  | Pr.06 | 1
[7 empty] | 17-I-DD-N-117BL02 | 06 Pair | TS-G-18 | 17-MC-DCS-007 |  | Pr.07 | 1
[7 empty] | 17-I-DD-N-118BL02 | 06 Pair | TS-G-19 | 17-MC-DCS-007 |  | Pr.08 | 1
[7 empty] | 17-I-DE-N-007BL02 | 01 Pair | TS-F-09 | 17-MC-DCS-007 |  | Pr.10 | 1
[7 empty] | 17-I-DE-N-008BL02 | 12 Pair | TS-F-10 | 17-MC-DCS-007 |  | Pr.11 | 1
[7 empty] | 17-J-DD-N-001FL11 | 06 Pair | TS-P-06 | 17-MC-DCS-002 |  | Pr.12 | 1
[7 empty] | 17-J-DD-N-002FL14 | 24 Pair | TS-Q-13 | 17-MC-DCS-002 |  | Pr.13 | 1
[7 empty] | 17-LT-03001 | 01 Pair | TS-P-05 | 17-MC-DCS-008 |  | Pr.14 | 1
[7 empty] | 17-LT-07077 | 01 Pair | TS-O-07 | 17-MC-DCS-006 | 17-C-AD-N-001FL11-L112 | Pr.01 | 1
[7 empty] | 17-LT-140025 | 01 Pair | TS-G-06 | 17-MC-DCS-009 |  | Pr.02 | 1
[7 empty] | 17-LZI-03003A | 01 Pair | TS-R-04 | 17-MC-DCS-006 |  | Pr.03 | 1
[7 empty] | 17-PDT-070173 | 01 Pair | TS-P-02 | 17-MC-DCS-006 |  | Pr.04 | 1
[7 empty] | 17-PDT-070174 | 01 Pair | TS-P-01 | 17-MC-DCS-006 |  | Pr.07 | 1
[7 empty] | 17-PT-11287 | 01 Pair | TS-Q-01 | 17-MC-DCS-008 |  | Pr.08 | 1
[7 empty] | 17-PY-17120 | 01 Pair | TS-H-02 | 17-MC-DCS-009 |  | Pr.09 | 1
[7 empty] | 17-TT -11264 | 01 Pair | TS-P-07 | 17-MC-DCS-008 |  | Pr.10 | 1
[7 empty] | 17-XY-07021 | 02 Core | TS-F-11 | 17-MC-DCS-007 |  | Pr.11 | 1
[7 empty] | 17-XY-07023 | 02 Core | TS-F-12 | 17-MC-DCS-007 |  | Pr.12 | 1
[7 empty] | 17-XY-09005 | 02 Core | TS-F-13 | 17-MC-DCS-007 | 17-C-AD-N-001FL17 | Pr.01 | 1
[7 empty] | 17-XY-17101 | 02 Core | TS-F-14 | 17-MC-DCS-007 |  | Pr.02 | 1
[7 empty] | 17-XZSH/L-09005 | 02 Pair | TS-G-07 | 17-MC-DCS-009 |  | Pr.03 | 1
[7 empty] | 17-XZSH/L-17101 | 02 Pair | TS-P-09 | 17-MC-DCS-002 |  | Pr.04 | 1
[7 empty] | 17-С-AD-I-1-FL90 | 15 Pair | TS-H-05 | 17-MC-DCS-009 |  | Pr.05 | 1
[7 empty] | 17-С-AD-N-1-FL90 | 05 Pair | TS-P-06 | 17-MC-DCS-008 |  | Pr.06 | 1
[7 empty] | (пусто) | (пусто) | (пусто) | 17-MC-DCS-001 |  | Pr.07 | 1
[10 empty] | 17-MC-DCS-002 |  | Pr.08 | 1
[10 empty] | 17-MC-DCS-003 |  | Pr.09 | 1
[10 empty] | 17-MC-DCS-004 |  | Pr.10 | 1
[10 empty] | 17-MC-DCS-005 |  | Pr.11 | 1
[10 empty] | 17-MC-DCS-006 |  | Pr.12 | 1
[10 empty] | 17-MC-DCS-007 |  | Pr.13 | 1
[10 empty] | 17-MC-DCS-008 |  | Pr.14 | 1
[10 empty] | 17-MC-DCS-009 |  | Pr.15 | 1
[7 empty] | 17-I-DD-N-119BL02 | 06 Pair | TS-F-19 | 17-MC-DCS-007 | 17-C-AD-N-001-LP003-L111 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[11 empty] | 17-C-AD-N-002FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[11 empty] | 17-C-AD-N-002FL07 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[11 empty] | 17-C-AD-N-002FL07-L073 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-C-AD-N-002FL10 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.15 | 1
[11 empty] | 17-C-AD-N-002FL11-L111 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[11 empty] | 17-C-AD-N-002FL14 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[11 empty] | 17-C-AD-N-003FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[11 empty] | 17-C-AD-N-003FL07-L073 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-C-AD-N-003FL10 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[11 empty] | 17-C-AD-N-003FL11-L111 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[11 empty] | 17-C-AD-N-004FL07-L073 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-C-AD-N-004FL10 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[11 empty] | 17-C-AD-N-005FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-C-AD-N-005FL07-L073 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-C-AD-N-006FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[11 empty] | 17-C-AD-N-702FL11-L111 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[11 empty] | 17-C-AP-I-002FL10-L091 | Pr.05 | 1
[11 empty] | 17-C-CD-N-001FL03-L022 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[11 empty] | 17-C-CD-N-001FL07 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-C-CD-N-001FL07-L073 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[11 empty] | 17-C-CD-N-001FL10 | C.01 | 1
[12 empty] | C.03 | 1
[11 empty] | 17-C-CD-N-002FL03-L022 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[11 empty] | 17-C-CD-N-002FL07 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-C-CD-N-002FL10 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-C-CD-N-003FL03-L022 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[11 empty] | 17-C-CD-N-003FL07 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-C-CD-N-004FL03-L022 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[11 empty] | 17-C-CD-N-005FL03-L022 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[11 empty] | 17-C-CD-N-006FL03-L022 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[11 empty] | 17-C-CD-N-006FL10-L091 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[12 empty] | C.27 | 1
[11 empty] | 17-C-CD-N-007FL03-L022 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[11 empty] | 17-C-CD-N-009FL03-L022 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[11 empty] | 17-C-CD-N-010FL03-L022 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[11 empty] | 17-C-DB-N-001FL11-L111 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-C-DD-001-LP001-K101 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[11 empty] | 17-C-DD-002-LP001-K101 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[11 empty] | 17-C-DD-I-005FL10-L091 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[11 empty] | 17-C-DD-N-001FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[11 empty] | 17-C-DD-N-001FL07 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[11 empty] | 17-C-DD-N-001FL10 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-C-DD-N-001FL11-AH001 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-C-DD-N-001FL11-L111 | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-C-DD-N-001FL14 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[11 empty] | 17-C-DD-N-001-LP001-P111A | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[11 empty] | 17-C-DD-N-001-LP002-L111 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.09 | 1
[11 empty] | 17-C-DD-N-001-LP003A-L091 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-C-DD-N-001-LP003B-L091 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-C-DD-N-001-LP003-L111 | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[11 empty] | 17-C-DD-N-002FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[11 empty] | 17-C-DD-N-002FL07 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[11 empty] | 17-C-DD-N-002FL10 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[11 empty] | 17-C-DD-N-002FL11-L111 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[11 empty] | 17-C-DD-N-002FL11-L111-CD | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[11 empty] | 17-C-DD-N-002-LP001-P111A | C.01 | 1
[11 empty] | 17-C-DD-N-002-LP002-L111 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[11 empty] | 17-C-DD-N-002-LP003A-L091 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.11 | 1
[11 empty] | 17-C-DD-N-002-LP003B-L091 | C.01 | 1
[11 empty] | 17-C-DD-N-003FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[11 empty] | 17-C-DD-N-003FL07 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[11 empty] | 17-C-DD-N-003FL10 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[11 empty] | 17-C-DD-N-003FL11-L111 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[11 empty] | 17-C-DD-N-003-LP001-P111A | C.01 | 1
[11 empty] | 17-C-DD-N-004FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[11 empty] | 17-C-DD-N-004FL10 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[11 empty] | 17-C-DD-N-005FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[11 empty] | 17-C-DD-N-006FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[11 empty] | 17-C-DD-N-007FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[11 empty] | 17-C-DD-N-009FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[11 empty] | 17-C-DD-N-010FL03-L022 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[11 empty] | 17-C-DD-N-1-FL50 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-C-RD-N-002FL10-K101 | Tr.01 | 1
[12 empty] | Tr.02 | 1
[12 empty] | Tr.03 | 1
[12 empty] | Tr.04 | 1
[12 empty] | Tr.05 | 1
[11 empty] | 17-C-XD-N-707FL11-L111 | Tr.01 | 1
[12 empty] | Tr.02 | 1
[11 empty] | 17-C-СD-N-1-FL50 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[11 empty] | 17-FSL -11101 | Pr.01 | 1
[11 empty] | 17-FSL-17101-CV | Pr.01 | 1
[11 empty] | 17-I-AD-N-001BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[11 empty] | 17-I-CD-N-001BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-I-CD-N-002BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-I-CD-N-003BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-I-CD-N-004BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[11 empty] | 17-I-CD-N-005BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-I-CD-N-006BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[11 empty] | 17-I-CD-N-007BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[11 empty] | 17-I-CD-N-008BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[12 empty] | C.27 | 1
[11 empty] | 17-I-CD-N-009BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-I-CD-N-010BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[11 empty] | 17-I-CD-N-011BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[12 empty] | C.27 | 1
[11 empty] | 17-I-CD-N-012BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[12 empty] | C.27 | 1
[11 empty] | 17-I-CD-N-013BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[12 empty] | C.27 | 1
[11 empty] | 17-I-CD-N-014BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[11 empty] | 17-I-CD-N-015BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[11 empty] | 17-I-CD-N-016BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-I-CD-N-017BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[11 empty] | 17-I-CD-N-018BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[11 empty] | 17-I-CD-N-019BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[11 empty] | 17-I-CD-N-020BL02 | C.01 | 1
[12 empty] | C.03 | 1
[11 empty] | 17-I-CD-N-021BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[11 empty] | 17-I-CD-N-022BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[12 empty] | C.13 | 1
[12 empty] | C.15 | 1
[12 empty] | C.17 | 1
[12 empty] | C.19 | 1
[12 empty] | C.21 | 1
[12 empty] | C.23 | 1
[12 empty] | C.25 | 1
[12 empty] | C.27 | 1
[11 empty] | 17-I-CD-N-023BL02 | C.01 | 1
[12 empty] | C.03 | 1
[12 empty] | C.05 | 1
[12 empty] | C.07 | 1
[12 empty] | C.09 | 1
[12 empty] | C.11 | 1
[11 empty] | 17-I-DD-N-001BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[12 empty] | Pr.22 | 1
[12 empty] | Pr.23 | 1
[11 empty] | 17-I-DD-N-001BL02-L091 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[11 empty] | 17-I-DD-N-001-BL02-L091 | Pr.06 | 1
[11 empty] | 17-I-DD-N-001-BL02-L101 | C.01 | 1
[11 empty] | 17-I-DD-N-002BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[12 empty] | Pr.22 | 1
[11 empty] | 17-I-DD-N-002BL02-L091 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[11 empty] | 17-I-DD-N-002-BL02-L101 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-I-DD-N-003BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[12 empty] | Pr.22 | 1
[11 empty] | 17-I-DD-N-004BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[11 empty] | 17-I-DD-N-005BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[11 empty] | 17-I-DD-N-006BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[11 empty] | 17-I-DD-N-007BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[11 empty] | 17-I-DD-N-008BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[11 empty] | 17-I-DD-N-009BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[11 empty] | 17-I-DD-N-010BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[11 empty] | 17-I-DD-N-011BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[11 empty] | 17-I-DD-N-012BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[11 empty] | 17-I-DD-N-013BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[11 empty] | 17-I-DD-N-014BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[11 empty] | 17-I-DD-N-015BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[11 empty] | 17-I-DD-N-016BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[11 empty] | 17-I-DD-N-017BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[11 empty] | 17-I-DD-N-018BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[11 empty] | 17-I-DD-N-019BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[11 empty] | 17-I-DD-N-020BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[11 empty] | 17-I-DD-N-021BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[12 empty] | Pr.13 | 1
[12 empty] | Pr.14 | 1
[12 empty] | Pr.15 | 1
[12 empty] | Pr.16 | 1
[12 empty] | Pr.17 | 1
[12 empty] | Pr.18 | 1
[12 empty] | Pr.19 | 1
[12 empty] | Pr.20 | 1
[12 empty] | Pr.21 | 1
[11 empty] | 17-I-DD-N-022BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-I-DD-N-023BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[11 empty] | 17-I-DD-N-024BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[11 empty] | 17-I-DD-N-101BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-I-DD-N-102BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-I-DD-N-103BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-104BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-105BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-106BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-107BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-108BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-109BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-110BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-111BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-112BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-113BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-114BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-115BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-I-DD-N-116BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-I-DD-N-117BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DD-N-118BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[11 empty] | 17-I-DE-N-007BL02 | Pr.01 | 1
[11 empty] | 17-I-DE-N-008BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[11 empty] | 17-J-DD-N-001FL11 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[11 empty] | 17-J-DD-N-002FL14 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.08 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[12 empty] | Pr.11 | 1
[12 empty] | Pr.12 | 1
[11 empty] | 17-LT-03001 | Pr.01 | 1
[11 empty] | 17-LT-07077 | Pr.01 | 1
[11 empty] | 17-LT-140025 | Pr.01 | 1
[11 empty] | 17-LZI-03003A | Pr.01 | 1
[11 empty] | 17-PDT-070173 | Pr.01 | 1
[11 empty] | 17-PDT-070174 | Pr.01 | 1
[11 empty] | 17-PT-11287 | Pr.01 | 1
[11 empty] | 17-PY-17120 | Pr.01 | 1
[11 empty] | 17-TT -11264 | Pr.01 | 1
[11 empty] | 17-XY-07021 | C.01 | 1
[11 empty] | 17-XY-07023 | C.01 | 1
[11 empty] | 17-XY-09005 | C.01 | 1
[11 empty] | 17-XY-17101 | C.01 | 1
[11 empty] | 17-XZSH/L-09005 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[11 empty] | 17-XZSH/L-17101 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[11 empty] | 17-С-AD-I-1-FL90 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1
[12 empty] | Pr.04 | 1
[12 empty] | Pr.05 | 1
[12 empty] | Pr.06 | 1
[12 empty] | Pr.07 | 1
[12 empty] | Pr.09 | 1
[12 empty] | Pr.10 | 1
[11 empty] | 17-С-AD-N-1-FL90 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[11 empty] | (пусто) | (пусто) | 525
[11 empty] | 17-I-DD-N-119BL02 | Pr.01 | 1
[12 empty] | Pr.02 | 1
[12 empty] | Pr.03 | 1

## Проверка
CABINET_MAR | FTS_NAME | FTS_TYPE | MAX TERMINAL | CABINET_MAR | STB_PART | STB_NAME | CABINET_MAR | BARRIER_MODEL | BARRIER_NAME | CABINET_SYS | MODULE_TYPE | MODULE
17-MC-DCS-001 | TS-F-01 | AVK 2,5 A, AVK 2,5 A | 48 | 17-MC-DCS-001 | TUA711-DIO32 | O1010203 | 17-MC-DCS-001 |  |  | 17-SC-DCS-001 | AI713-H11 | O1010000
| TS-F-02 | AVK 2,5 A, AVK 2,5 A | 48 |  | TUA711-DIR32 | O1010200 |  | HD5516 | O1010203_U1 |  |  | O1010001
| TS-F-03 | AVK 2,5 A, AVK 2,5 A | 12 |  |  | O1010201 |  |  | O1010203_U10 |  |  | O1010002
| TS-F-04 | AVK 2,5 A, AVK 2,5 A | 24 |  |  | O1010202 |  |  | O1010203_U11 |  |  | O1010003
| TS-F-05 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1010304R |  |  | O1010203_U12 |  |  | O1010004
| TS-F-06 | AVK 2,5 A, AVK 2,5 A | 48 |  | TUA711-DOR32 | O1010210 |  |  | O1010203_U13 |  |  | O1010005
| TS-G-01 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1010211 |  |  | O1010203_U14 |  |  | O1010006
| TS-G-02 | AVK 2,5 A, AVK 2,5 A | 16 |  |  | O1011212 |  |  | O1010203_U15 |  |  | O1010007
| TS-G-03 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1010304R |  |  | O1010203_U16 |  |  | O1010008
| TS-G-04 | AVK 2,5 A, AVK 2,5 A | 30 | 17-MC-DCS-002 | TUA711-DIO32 | O1011100 |  |  | O1010203_U17 |  |  | O1010009
| TS-G-05 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1011101 |  |  | O1010203_U18 |  |  | O1010010
| TS-G-06 | AVK 2,5 A, AVK 2,5 A | 12 |  |  | O1011102 |  |  | O1010203_U19 |  |  | O1010011
| TS-G-07 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1011103 |  |  | O1010203_U2 |  |  | O1010012R
| TS-G-08 | AVK 2,5 A, AVK 2,5 A | 24 |  |  | O1011104 |  |  | O1010203_U20 |  |  | O1010014R
| TS-H-01 | AVK 2,5 A, AVK 2,5 A | 48 |  | TUA711-DIR32 | O1010204 |  |  | O1010203_U21 |  |  | O1010100R
| TS-H-02 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1011105 |  |  | O1010203_U22 |  |  | O1010102R
| TS-H-03 | AVK 2,5 A, AVK 2,5 A | 20 |  | TUA711-DOR32 | O1011202 |  |  | O1010203_U23 |  | AO713-H11 | O1010104R
| TS-H-04 | AVK 2,5 A, AVK 2,5 A | 20 |  |  | O1011203 |  |  | O1010203_U24 |  |  | O1010106R
| TS-H-05 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1011204 |  |  | O1010203_U25 |  |  | O1010108R
17-MC-DCS-002 | TS-O-01 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1010204 |  |  | O1010203_U26 |  |  | O1010110R
| TS-O-02 | AVK 2,5 A, AVK 2,5 A | 30 | 17-MC-DCS-003 | TUA711-DIO32 | O1010206 |  |  | O1010203_U27 |  |  | O1010112R
| TS-O-03 | AVK 2,5 A, AVK 2,5 A | 16 |  |  | O1010207 |  |  | O1010203_U3 |  |  | O1010114
| TS-O-04 | AVK 2,5 A, AVK 2,5 A | 16 |  |  | O1010208 |  |  | O1010203_U4 |  | DI715-S11 | O1010115
| TS-O-05 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1010212 |  |  | O1010203_U5 |  |  | O1010200
| TS-O-06 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1010213 |  |  | O1010203_U6 |  |  | O1010201
| TS-O-07 | AVK 2,5 A, AVK 2,5 A | 24 |  |  | O1010214 |  |  | O1010203_U7 |  |  | O1010202
| TS-O-08 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1011213 |  |  | O1010203_U8 |  |  | O1010203
| TS-O-09 | AVK 2,5 A, AVK 2,5 A | 24 | 17-MC-DCS-004 | TUA711-DIO32 | O1010205 |  |  | O1010203_U9 |  |  | O1010204
| TS-P-01 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1010301 |  | KFD2-ER-1.W.LB | O1010203_U28 |  |  | O1010205
| TS-P-02 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1011106 |  |  | O1010203_U29 |  |  | O1010206
| TS-P-03 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1011107 |  |  | O1010203_U30 |  |  | O1010207
| TS-P-04 | AVK 2,5 A, AVK 2,5 A | 30 |  |  | O1011108 |  |  | O1010203_U31 |  |  | O1010208
| TS-P-05 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1011109 |  |  | O1010203_U32 |  |  | O1010209
| TS-P-06 | AVK 2,5 A, AVK 2,5 A | 12 |  |  | O1011110 |  | (пусто) |  |  |  | O1010300
| TS-P-07 | AVK 2,5 A, AVK 2,5 A | 12 |  |  | O1011205 |  |  | (пусто) |  |  | O1010301
| TS-Q-01 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1011206 | 17-MC-DCS-002 |  |  |  |  | O1010304R
| TS-Q-02 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1011207 |  | HD5516 | O1011100_U1 |  | DO716-S11 | O1010210
| TS-Q-03 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1011208 |  |  | O1011100_U10 |  |  | O1010211
| TS-Q-04 | AVK 2,5 A, AVK 2,5 A | 24 | 17-MC-DCS-005 | TUA711-DIO32 | O1010115 |  |  | O1011100_U11 |  |  | O1010212
| TS-Q-05 | AVK 2,5 A, AVK 2,5 A | 2 |  |  | O1010209 |  |  | O1011100_U12 |  |  | O1010213
| TS-Q-06 | AVK 2,5 A, AVK 2,5 A | 2 |  |  | O1010215 |  |  | O1011100_U13 |  |  | O1010214
| TS-Q-07 | AVK 2,5 A, AVK 2,5 A | 2 |  |  | O1010300 |  |  | O1011100_U14 |  |  | O1010215
| TS-Q-08 | AVK 2,5 A, AVK 2,5 A | 2 |  |  | O1011111 |  |  | O1011100_U15 | 17-SC-DCS-002 | AI713-H11 | O1011000
| TS-Q-09 | AVK 2,5 A, AVK 2,5 A | 2 |  |  | O1011112 |  |  | O1011100_U16 |  |  | O1011001
| TS-Q-10 | AVK 2,5 A, AVK 2,5 A | 2 |  |  | O1011209 |  |  | O1011100_U2 |  |  | O1011002
| TS-Q-11 | AVK 2,5 A, AVK 2,5 A | 2 |  |  | O1011304 |  |  | O1011100_U3 |  |  | O1011003
| TS-Q-12 | AVK 2,5 A, AVK 2,5 A | 2 | 17-MC-DCS-006 | TUA711-AIO16 | O1010000 |  |  | O1011100_U4 |  |  | O1011004
| TS-R-01 | AVK 2,5 A, AVK 2,5 A | 24 |  |  | O1010001 |  |  | O1011100_U5 |  |  | O1011005
| TS-R-02 | AVK 2,5 A, AVK 2,5 A | 24 |  |  | O1010002 |  |  | O1011100_U6 |  |  | O1011006
| TS-R-03 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1010003 |  |  | O1011100_U7 |  |  | O1011008R
| TS-R-04 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1010004 |  |  | O1011100_U8 |  |  | O1011010R
| TS-Q-13 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1010005 |  |  | O1011100_U9 |  |  | O1011300R
| TS-Q-14 | AVK 2,5 A, AVK 2,5 A | 48 |  |  | O1010006 |  |  | O1011101_U1 |  | AO713-H11 | O1011012R
| TS-P-08 | AVK 2,5 A, AVK 2,5 A | 12 |  |  | O1010007 |  |  | O1011101_U10 |  |  | O1011014R
| TS-P-09 | AVK 2,5 A, AVK 2,5 A | 4 |  |  | O1010008 |  |  | O1011101_U11 |  |  | O1011302R
| TS-O-10 | AVK 2,5 A, AVK 2,5 A | 12 |  |  | O1010012R |  |  | O1011101_U12 |  | DI715-S11 | O1011100
17-MC-DCS-003 | TS-F-01 | ASK 3MLD, ASK 3MB | 16 |  |  | O1010014R |  |  | O1011101_U13 |  |  | O1011101
| TS-F-02 | ASK 3MLD, ASK 3MB | 48 |  |  | O1010104R |  |  | O1011101_U14 |  |  | O1011102
| TS-F-03 | ASK 3MLD, ASK 3MB | 48 |  |  | O1010106R |  |  | O1011101_U15 |  |  | O1011103
| TS-F-04 | ASK 3MLD, ASK 3MB | 48 |  |  | O1010114 |  |  | O1011101_U16 |  |  | O1011104
| TS-F-05 | ASK 3MLD, ASK 3MB | 48 |  |  | O1011000 |  |  | O1011101_U17 |  |  | O1011105
| TS-G-01 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011012R |  |  | O1011101_U18 |  |  | O1011106
| TS-G-02 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011000 |  |  | O1011101_U19 |  |  | O1011107
| TS-G-03 | ASK 3MLD, ASK 3MB | 30 | 17-MC-DCS-007 | TUA711-AIO16 | O1011008R |  |  | O1011101_U2 |  |  | O1011108
| TS-G-04 | ASK 3MLD, ASK 3MB | 30 |  | TUA711-DIR32 | O1011113 |  |  | O1011101_U20 |  |  | O1011109
| TS-G-05 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011114 |  |  | O1011101_U21 |  |  | O1011110
| TS-G-06 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011200 |  |  | O1011101_U22 |  |  | O1011111
| TS-G-07 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011201 |  |  | O1011101_U23 |  |  | O1011112
| TS-G-08 | ASK 3MLD, ASK 3MB | 30 |  | TUA711-DOR32 | O1011210 |  |  | O1011101_U24 |  |  | O1011113
| TS-H-01 | ASK 3MLD, ASK 3MB | 48 |  |  | O1011211 |  |  | O1011101_U25 |  |  | O1011114
17-MC-DCS-004 | TS-O-01 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011114 |  |  | O1011101_U26 |  |  | O1011115
| TS-O-02 | ASK 3MLD, ASK 3MB | 30 | 17-MC-DCS-008 | TUA711-AIO16 | O1010009 |  |  | O1011101_U27 |  |  | O1011200
| TS-O-03 | ASK 3MLD, ASK 3MB | 30 |  |  | O1010010 |  |  | O1011101_U28 |  |  | O1011201
| TS-O-04 | ASK 3MLD, ASK 3MB | 30 |  |  | O1010100R |  |  | O1011101_U29 |  |  | O1011304
| TS-O-05 | ASK 3MLD, ASK 3MB | 48 |  |  | O1010108R |  |  | O1011101_U3 |  | DO716-S11 | O1011202
| TS-O-06 | ASK 3MLD, ASK 3MB | 48 |  |  | O1011001 |  |  | O1011101_U30 |  |  | O1011203
| TS-P-01 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011002 |  |  | O1011101_U31 |  |  | O1011204
| TS-P-02 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011003 |  |  | O1011101_U32 |  |  | O1011205
| TS-P-03 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011004 |  |  | O1011101_U4 |  |  | O1011206
| TS-P-04 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011010R |  |  | O1011101_U5 |  |  | O1011207
| TS-P-05 | ASK 3MLD, ASK 3MB | 30 |  |  | O1011014R |  |  | O1011101_U6 |  |  | O1011208
| TS-P-06 | ASK 3MLD, ASK 3MB | 24 |  |  | O1011302R |  |  | O1011101_U7 |  |  | O1011209
| TS-P-07 | ASK 3MLD, ASK 3MB | 16 |  |  | (пусто) |  |  | O1011101_U8 |  |  | O1011210
| TS-Q-01 | ASK 3MLD, ASK 3MB | 48 | 17-MC-DCS-009 | TUA711-AIO16 | O1010011 |  |  | O1011101_U9 |  |  | O1011211
| TS-Q-02 | AVK 2,5 A, AVK 2,5 A | 24 |  |  | O1010102R |  |  | O1011102_U1 |  |  | O1011212
| TS-R-01 | ASK 3MLD, ASK 3MB | 48 |  |  | O1010110R |  |  | O1011102_U10 |  |  | O1011213
| TS-R-02 | ASK 3MLD, ASK 3MB | 48 |  |  | O1010112R |  |  | O1011102_U11 | (пусто) | (пусто) | (пусто)
| TS-R-03 | ASK 3MLD, ASK 3MB | 48 |  |  | O1011005 |  |  | O1011102_U12
| TS-R-04 | ASK 3MLD, ASK 3MB | 48 |  |  | O1011006 |  |  | O1011102_U13
| TS-R-05 | ASK 3MLD, ASK 3MB | 48 |  |  | O1011300R |  |  | O1011102_U14
17-MC-DCS-005 | TS-F-01 | ASK 3MLD, ASK 3MB | 48 |  | TUA711-DIO32 | O1011115 |  |  | O1011102_U15
| TS-F-02 | ASK 3MLD, ASK 3MB | 48 | (пусто) | (пусто) | (пусто) |  |  | O1011102_U16
| TS-F-03 | ASK 3MLD, ASK 3MB | 48 | [5 empty] | O1011102_U17
| TS-F-04 | ASK 3MLD, ASK 3MB | 48 | [5 empty] | O1011102_U18
| TS-G-01 | ASK 3MLD, ASK 3MB | 48 | [5 empty] | O1011102_U19
| TS-G-02 | ASK 3MLD, ASK 3MB | 48 | [5 empty] | O1011102_U2
| TS-G-03 | ASK 3MLD, ASK 3MB | 48 | [5 empty] | O1011102_U20
| TS-G-04 | ASK 3MLD, ASK 3MB | 48 | [5 empty] | O1011102_U21
| TS-H-01 | ASK 3MLD, ASK 3MB | 30 | [5 empty] | O1011102_U22
| TS-H-02 | ASK 3MLD, ASK 3MB | 30 | [5 empty] | O1011102_U23
| TS-H-03 | ASK 3MLD, ASK 3MB | 30 | [5 empty] | O1011102_U24
| TS-H-04 | ASK 3MLD, ASK 3MB | 30 | [5 empty] | O1011102_U25
17-MC-DCS-006 | TS-O-01 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011102_U26
| TS-O-02 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011102_U27
| TS-O-03 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011102_U28
| TS-O-04 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011102_U29
| TS-O-05 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011102_U3
| TS-O-06 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011102_U30
| TS-O-07 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011102_U31
| TS-P-01 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011102_U32
| TS-P-02 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011102_U4
| TS-Q-01 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011102_U5
| TS-Q-02 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011102_U6
| TS-Q-03 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011102_U7
| TS-Q-04 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011102_U8
| TS-Q-05 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011102_U9
| TS-Q-06 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U1
| TS-Q-07 | AVK 2,5 A, AVK 2,5 A, AVK 2,5 A | 18 | [5 empty] | O1011103_U10
| TS-Q-08 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011103_U11
| TS-R-01 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011103_U12
| TS-R-02 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U13
| TS-R-03 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011103_U14
| TS-R-04 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011103_U15
| TS-R-05 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011103_U16
17-MC-DCS-007 | TS-F-01 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011103_U17
| TS-F-02 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011103_U18
| TS-F-03 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U19
| TS-F-04 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U2
| TS-F-05 | AVK 2,5 A, AVK 2,5 A | 4 | [5 empty] | O1011103_U20
| TS-F-06 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U21
| TS-F-07 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U22
| TS-F-08 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U23
| TS-F-09 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011103_U24
| TS-F-10 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011103_U25
| TS-F-11 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011103_U26
| TS-F-12 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011103_U27
| TS-F-13 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011103_U28
| TS-F-14 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011103_U29
| TS-F-15 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U3
| TS-F-16 | AVK 2,5 A, AVK 2,5 A | 18 | [5 empty] | O1011103_U30
| TS-F-17 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U31
| TS-F-18 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U32
| TS-G-01 | AVK 2,5 A, AVK 2,5 A | 30 | [5 empty] | O1011103_U4
| TS-G-02 | AVK 2,5 A, AVK 2,5 A | 8 | [5 empty] | O1011103_U5
| TS-G-03 | AVK 2,5 A, AVK 2,5 A | 16 | [5 empty] | O1011103_U6
| TS-G-04 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U7
| TS-G-05 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U8
| TS-G-06 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011103_U9
| TS-G-07 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U1
| TS-G-08 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U10
| TS-G-09 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U11
| TS-G-10 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U12
| TS-G-11 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U13
| TS-G-12 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U14
| TS-G-13 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U15
| TS-G-14 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U16
| TS-G-15 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U17
| TS-G-16 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U18
| TS-G-17 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U19
| TS-G-18 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U2
| TS-G-19 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U20
| TS-H-01 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011104_U21
| TS-H-02 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011104_U22
| TS-H-03 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011104_U23
| TS-H-04 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U24
| TS-H-05 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U25
| TS-H-06 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U26
| TS-H-07 | AVK 2,5 A, AVK 2,5 A | 30 | [5 empty] | O1011104_U27
| TS-H-08 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011104_U28
17-MC-DCS-008 | TS-O-01 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011104_U29
| TS-O-02 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011104_U3
| TS-O-03 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011104_U30
| TS-O-04 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U31
| TS-O-05 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011104_U4
| TS-O-06 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011104_U5
| TS-O-07 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U6
| TS-O-08 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U7
| TS-O-09 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011104_U8
| TS-P-01 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011104_U9
| TS-P-02 | AVK 2,5 A, AVK 2,5 A | 48 |  |  |  |  | KFD2-ER-1.W.LB | O1011100_U17
| TS-P-03 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011100_U18
| TS-P-04 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011100_U19
| TS-P-05 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011100_U20
| TS-P-06 | AVK 2,5 A, AVK 2,5 A | 10 | [5 empty] | O1011100_U21
| TS-P-07 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011100_U22
| TS-Q-01 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011100_U23
17-MC-DCS-009 | TS-G-01 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011100_U24
| TS-G-02 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011100_U25
| TS-G-03 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011100_U26
| TS-G-04 | AVK 2,5 A, AVK 2,5 A | 24 | [5 empty] | O1011100_U27
| TS-G-05 | AVK 2,5 A, AVK 2,5 A | 48 | [5 empty] | O1011100_U28
| TS-G-06 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011100_U29
| TS-G-07 | AVK 2,5 A, AVK 2,5 A | 4 | [5 empty] | O1011100_U30
| TS-G-08 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011100_U31
| TS-H-01 | AVK 2,5 A, AVK 2,5 A | 12 | [5 empty] | O1011100_U32
| TS-H-02 | AVK 2,5 A, AVK 2,5 A | 2 | [5 empty] | O1011104_U32
| TS-H-03 | AVK 2,5 A, AVK 2,5 A | 48 |  |  |  | 17-MC-DCS-003
| TS-H-04 | AVK 2,5 A, AVK 2,5 A | 48 |  |  |  | 17-MC-DCS-004
| TS-H-05 | AVK 2,5 A, AVK 2,5 A | 30 |  |  |  |  | HD5516 | O1010205_U1
O1010205_U10
O1010205_U11
O1010205_U12
O1010205_U13
O1010205_U14
O1010205_U15
O1010205_U16
O1010205_U17
O1010205_U18
O1010205_U19
O1010205_U2
O1010205_U20
O1010205_U21
O1010205_U22
O1010205_U23
O1010205_U24
O1010205_U25
O1010205_U26
O1010205_U27
O1010205_U28
O1010205_U29
O1010205_U3
O1010205_U30
O1010205_U31
O1010205_U32
O1010205_U4
O1010205_U5
O1010205_U6
O1010205_U7
O1010205_U8
O1010205_U9
O1011110_U25
O1011110_U26
O1011110_U27
O1011110_U28
O1011110_U29
O1011110_U30
O1011110_U31
17-MC-DCS-005
[8 empty] | (пусто) | (пусто)
17-MC-DCS-006
[8 empty] | HD5542 | O1010000_U1
O1010000_U10
O1010000_U11
O1010000_U12
O1010000_U13
O1010000_U14
O1010000_U15
O1010000_U16
O1010000_U2
O1010000_U3
O1010000_U4
O1010000_U5
O1010000_U6
O1010000_U7
O1010000_U8
O1010000_U9
O1010001_U1
O1010001_U10
O1010001_U11
O1010001_U12
O1010001_U13
O1010001_U14
O1010001_U15
O1010001_U16
O1010001_U2
O1010001_U3
O1010001_U4
O1010001_U5
O1010001_U6
O1010001_U7
O1010001_U8
O1010001_U9
O1010002_U1
O1010002_U10
O1010002_U11
O1010002_U12
O1010002_U13
O1010002_U14
O1010002_U15
O1010002_U16
O1010002_U2
O1010002_U3
O1010002_U4
O1010002_U5
O1010002_U6
O1010002_U7
O1010002_U8
O1010002_U9
O1010003_U1
O1010003_U10
O1010003_U11
O1010003_U12
O1010003_U13
O1010003_U14
O1010003_U15
O1010003_U16
O1010003_U2
O1010003_U3
O1010003_U4
O1010003_U5
O1010003_U6
O1010003_U7
O1010003_U8
O1010003_U9
O1010004_U1
O1010004_U10
O1010004_U11
O1010004_U12
O1010004_U13
O1010004_U14
O1010004_U15
O1010004_U16
O1010004_U2
O1010004_U3
O1010004_U4
O1010004_U5
O1010004_U6
O1010004_U7
O1010004_U8
O1010004_U9
O1010005_U1
O1010005_U10
O1010005_U11
O1010005_U12
O1010005_U13
O1010005_U14
O1010005_U15
O1010005_U16
O1010005_U2
O1010005_U3
O1010005_U4
O1010005_U5
O1010005_U6
O1010005_U7
O1010005_U8
O1010005_U9
O1010006_U1
O1010006_U10
O1010006_U11
O1010006_U12
O1010006_U13
O1010006_U14
O1010006_U15
O1010006_U16
O1010006_U2
O1010006_U3
O1010006_U4
O1010006_U5
O1010006_U6
O1010006_U7
O1010006_U8
O1010006_U9
O1010007_U1
O1010007_U10
O1010007_U11
O1010007_U12
O1010007_U13
O1010007_U14
O1010007_U15
O1010007_U16
O1010007_U2
O1010007_U3
O1010007_U4
O1010007_U5
O1010007_U6
O1010007_U7
O1010007_U8
O1010007_U9
O1010008_U10
O1010008_U11
O1010008_U12
O1010008_U13
O1010008_U14
O1010008_U15
O1010008_U16
O1010008_U7
O1010008_U8
O1010008_U9
O1010012R_U1
O1010012R_U10
O1010012R_U11
O1010012R_U12
O1010012R_U13
O1010012R_U14
O1010012R_U15
O1010012R_U16
O1010012R_U2
O1010012R_U3
O1010012R_U4
O1010012R_U5
O1010012R_U6
O1010012R_U7
O1010012R_U8
O1010012R_U9
O1010014R_U1
O1010014R_U10
O1010014R_U11
O1010014R_U12
O1010014R_U13
O1010014R_U14
O1010014R_U15
O1010014R_U16
O1010014R_U2
O1010014R_U3
O1010014R_U4
O1010014R_U5
O1010014R_U6
O1010014R_U7
O1010014R_U8
O1010014R_U9
O1011000_U1
O1011000_U2
O1011000_U3
O1011000_U4
O1011000_U5
O1011000_U6
O1011000_U7
O1011000_U8
[8 empty] | HD5546 | O1010104R_U1
O1010104R_U10
O1010104R_U11
O1010104R_U12
O1010104R_U13
O1010104R_U14
O1010104R_U15
O1010104R_U16
O1010104R_U2
O1010104R_U3
O1010104R_U4
O1010104R_U5
O1010104R_U6
O1010104R_U7
O1010104R_U8
O1010104R_U9
O1010106R_U1
O1010106R_U10
O1010106R_U11
O1010106R_U12
O1010106R_U13
O1010106R_U14
O1010106R_U15
O1010106R_U16
O1010106R_U2
O1010106R_U3
O1010106R_U4
O1010106R_U5
O1010106R_U6
O1010106R_U7
O1010106R_U8
O1010106R_U9
O1010114_U1
O1010114_U2
O1010114_U3
O1010114_U4
O1010114_U5
O1011012R_U1
O1011012R_U10
O1011012R_U11
O1011012R_U12
O1011012R_U2
O1011012R_U3
O1011012R_U4
O1011012R_U5
O1011012R_U6
O1011012R_U7
O1011012R_U8
O1011012R_U9
[8 empty] | HD5573 | O1010008_U1
O1010008_U2
O1010008_U3
O1010008_U4
O1010008_U5
O1010008_U6
[8 empty] | (пусто) | (пусто)
17-MC-DCS-007
[8 empty] | GS8555-EX | O1011008R_U1
O1011008R_U2
O1011008R_U3
[8 empty] | HD5542 | O1011008R_U10
O1011008R_U11
O1011008R_U12
O1011008R_U13
O1011008R_U14
O1011008R_U5
O1011008R_U6
O1011008R_U7
O1011008R_U8
O1011008R_U9
O1011008R_U4
17-MC-DCS-008
[8 empty] | HD5542 | O1010009_U1
O1010009_U10
O1010009_U11
O1010009_U12
O1010009_U13
O1010009_U14
O1010009_U15
O1010009_U16
O1010009_U2
O1010009_U3
O1010009_U4
O1010009_U5
O1010009_U6
O1010009_U7
O1010009_U8
O1010009_U9
O1010010_U1
O1010010_U10
O1010010_U11
O1010010_U12
O1010010_U13
O1010010_U14
O1010010_U15
O1010010_U16
O1010010_U2
O1010010_U3
O1010010_U4
O1010010_U5
O1010010_U6
O1010010_U7
O1010010_U8
O1010010_U9
O1010100R_U1
O1010100R_U2
O1010100R_U3
O1010100R_U4
O1010100R_U5
O1010100R_U6
O1011001_U1
O1011001_U10
O1011001_U11
O1011001_U12
O1011001_U13
O1011001_U14
O1011001_U15
O1011001_U16
O1011001_U2
O1011001_U3
O1011001_U4
O1011001_U5
O1011001_U6
O1011001_U7
O1011001_U8
O1011001_U9
O1011002_U1
O1011002_U10
O1011002_U11
O1011002_U12
O1011002_U13
O1011002_U14
O1011002_U15
O1011002_U16
O1011002_U2
O1011002_U3
O1011002_U4
O1011002_U5
O1011002_U6
O1011002_U7
O1011002_U8
O1011002_U9
O1011003_U1
O1011003_U10
O1011003_U11
O1011003_U12
O1011003_U13
O1011003_U14
O1011003_U15
O1011003_U16
O1011003_U2
O1011003_U3
O1011003_U4
O1011003_U5
O1011003_U6
O1011003_U7
O1011003_U8
O1011003_U9
O1011004_U1
O1011004_U10
O1011004_U11
O1011004_U12
O1011004_U13
O1011004_U14
O1011004_U15
O1011004_U16
O1011004_U2
O1011004_U3
O1011004_U4
O1011004_U5
O1011004_U6
O1011004_U7
O1011004_U8
O1011004_U9
O1011010R_U1
O1011010R_U10
O1011010R_U11
O1011010R_U12
O1011010R_U13
O1011010R_U14
O1011010R_U2
O1011010R_U3
O1011010R_U4
O1011010R_U5
O1011010R_U6
O1011010R_U7
O1011010R_U8
O1011010R_U9
[8 empty] | HD5546 | O1010108R_U1
O1010108R_U10
O1010108R_U11
O1010108R_U12
O1010108R_U13
O1010108R_U14
O1010108R_U2
O1010108R_U3
O1010108R_U4
O1010108R_U5
O1010108R_U6
O1010108R_U7
O1010108R_U8
O1010108R_U9
O1011014R_U1
O1011014R_U10
O1011014R_U11
O1011014R_U12
O1011014R_U13
O1011014R_U14
O1011014R_U15
O1011014R_U2
O1011014R_U3
O1011014R_U4
O1011014R_U5
O1011014R_U6
O1011014R_U7
O1011014R_U8
O1011014R_U9
O1011302R_U1
O1011302R_U2
O1011302R_U3
O1011302R_U4
O1011302R_U5
O1011302R_U6
O1011302R_U7
O1011302R_U8
O1011302R_U9
[8 empty] | (пусто) | (пусто)
17-MC-DCS-009
[8 empty] | HD5516 | O1011115_U1
O1011115_U10
O1011115_U11
O1011115_U12
O1011115_U13
O1011115_U14
O1011115_U15
O1011115_U16
O1011115_U17
O1011115_U18
O1011115_U19
O1011115_U2
O1011115_U20
O1011115_U21
O1011115_U22
O1011115_U23
O1011115_U3
O1011115_U4
O1011115_U5
O1011115_U6
O1011115_U7
O1011115_U8
O1011115_U9
[8 empty] | HD5542 | O1010011_U1
O1010011_U10
O1010011_U11
O1010011_U12
O1010011_U13
O1010011_U14
O1010011_U15
O1010011_U16
O1010011_U2
O1010011_U3
O1010011_U4
O1010011_U5
O1010011_U6
O1010011_U7
O1010011_U8
O1010011_U9
O1010102R_U1
O1010102R_U10
O1010102R_U11
O1010102R_U12
O1010102R_U13
O1010102R_U14
O1010102R_U15
O1010102R_U16
O1010102R_U2
O1010102R_U3
O1010102R_U4
O1010102R_U5
O1010102R_U6
O1010102R_U7
O1010102R_U8
O1010102R_U9
O1011005_U1
O1011005_U10
O1011005_U11
O1011005_U12
O1011005_U13
O1011005_U14
O1011005_U15
O1011005_U16
O1011005_U2
O1011005_U3
O1011005_U4
O1011005_U5
O1011005_U6
O1011005_U7
O1011005_U8
O1011005_U9
O1011006_U1
O1011006_U10
O1011006_U11
O1011006_U12
O1011006_U13
O1011006_U14
O1011006_U15
O1011006_U16
O1011006_U2
O1011006_U3
O1011006_U4
O1011006_U5
O1011006_U6
O1011006_U7
O1011006_U8
O1011006_U9
O1011300R_U1
O1011300R_U2
[8 empty] | HD5546 | O1010110R_U1
O1010110R_U10
O1010110R_U11
O1010110R_U12
O1010110R_U13
O1010110R_U14
O1010110R_U15
O1010110R_U16
O1010110R_U2
O1010110R_U3
O1010110R_U4
O1010110R_U5
O1010110R_U6
O1010110R_U7
O1010110R_U8
O1010110R_U9
O1010112R_U1
O1010112R_U2
O1010112R_U3
O1010112R_U4
O1010112R_U5
[8 empty] | (пусто) | (пусто)
[7 empty] | (пусто) | (пусто) | (пусто)